## Entries October'25
| ENTRIES FOR DAILY CONS. MONITOR | [12 empty] | ENTRIES FOR DAILY CONS. MONITOR
|  | old |  |  | old | [8 empty] | Service 227.3 cubic meters (2273 Hls)Filtered 189.3 cubic meters(1893 Hls)
|  |  | FUEL | [5 empty] | ELECT. |  | CO2 |  |  | WATER | [17 empty] | CO2 Scrubber (m3) | Supply to Washdown Area (m3) | Supply to RUs (m3) | Steam Mass Flow Meter | CO2 TANKS' READING
| Boilers tot. | Boiler 1 | Gen. meter | Tank level | Boiler 1 | Boiler 2 | Gen | Meter1 | Meter 2 | Gen Meter | Consumption (BMF) (kg) | Consumption (Totalizer Flowmeter) | Consumption (Filler) (kg) | Nawasa Meter (m3) | Annandale Supply (m3) | Service Supply to Plant (m3) | Cellars/Filtration (m3) | Brewhouse Meter (m3) | Cellars/Process Areas (m3) | Pasteuriser (m3) | Water Plant-Nawasa Annadale (m3) | Water Plant-Well # 1 (m3) | CIP Process | Bottle Washer | Boiler | Permeate #1 | Permeate #2 | Bottle Filler (m3) | RO # 1 Totaliser (m3) | RO # 2 Totaliser (m3) | Recovered Water (m3) |  |  |  |  | Tank "C" | Tank "A" | Tank "B" | Mobile Tanker
DATE | (liters) | (liters) | (Imp. gals) | (inches) | Hrs | Hrs | Hrs. | (Kwhr) | (Kwhr) | (Kwhr) |  | (kg) | [10 empty] | (m3) | (m3) | (m3) | [10 empty] | inH2O | (Kg.) | (Kg.) | (pounds)
1 | 7688000 |  |  | 64 | 5885.9 | 68225 |  | 126545 | 644115 | 468000 | 698.99 | 100759.27 | 16327.16 | 197585 | 37910 | 924266 |  | 58897 |  | 21369 | 1316136 |  | 38049 | 43045 | 9523 | 97122 |  | 1208 | 260317 | [5 empty] | 7305590.893
2 | 7691570 |  |  | 64 | 5907.4 | 68225 |  | 131708 | 648847 | 468000 | 748.08 | 103919.75 | 16825.28 | 197817 | 38101 | 924553 |  | 59158 |  | 21381 | 1316336 |  | 38101 | 43164 | 9544 | 97122 |  | 1240 | 260320 | [5 empty] | 7305590.893 | 220 | 0 | 0
3 | 7695230 |  |  | 64 | 5928.4 | 68225 |  | 136863 | 653573 | 468000 | 832.09 | 106991.08 | 17346.7 | 198068 | 38338 | 924847 |  | 59362 |  | 21404 | 1316586 |  | 38159 | 43282 | 9563 | 97122 |  | 1240 | 260350 | [5 empty] | 7305590.893 | 220 | 0 | 0
4 | 7698320 |  |  | 64 | 5946.7 | 68225 |  | 141805 | 658098 | 468000 | 876.07 | 108715.68 | 17633.6 | 198216 | 38536 | 925053 |  | 59585 |  | 21415 | 1316794 |  | 38198 | 43356 | 9580 | 97122 |  | 1289 | 260386 | [5 empty] | 7305590.893 | 190 | 0 | 0
5 | 7698320 |  |  | 64 | 5946.7 | 68225 |  | 144639 | 660626 | 468000 | 876.07 | 108715.68 | 17633.6 | 198226 | 38561 | 925120 |  | 59588 |  | 21415 | 1316820 |  | 38198 | 43394 | 9587 | 97122 |  | 1292 | 260386 | [5 empty] | 7305711.987 |  | 0 | 0
6 | 7698320 |  |  | 64 | 5946.7 | 68225 |  | 146515 | 662388 | 468000 | 876.07 | 108715.68 | 17633.6 | 198253 | 38658 | 925126 |  | 59588 |  | 21415 | 1316922 |  | 38198 | 43399 | 9587 | 97122 |  | 1292 | 260386 | [5 empty] | 7305711.987 |  | 0 | 0
7 | 7702140 |  |  | 64 | 5970.4 | 68225 |  | 151378 | 666843 | 468000 | 936.49 | 110656.23 | 17854.95 | 198472 | 38786 | 925337 |  | 59891 |  | 21430 | 1317056 |  | 38253 | 43465 | 9611 | 97122 |  | 1308 | 260464 | [5 empty] | 7305849.233 | 160 | 0 | 0
8 | 7704950 |  |  | 64 | 5988.7 | 68225 |  | 156142 | 671209 | 468000 | 977.51 | 112041.91 | 18097.68 | 198588 | 39037 | 925553 |  | 60113 |  | 21440 | 1317320 |  | 38297 | 43546 | 9624 | 97122 |  | 1325 | 260464 | [5 empty] | 7305849.233 | 140 | 0 | 0 | 42108.2993
9 | 7708280 |  |  | 64 | 6009.23 | 68225 |  | 160918 | 675585 | 468000 | 999.81 | 113781.22 | 18409.37 | 198822 | 39240 | 925805 |  | 60361 |  | 21451 | 1317534 |  | 38357 | 43642 | 9641 | 97122 |  | 1344 | 260475 | [5 empty] | 7305849.233 | 140 | 0 | 0 | 21974
10 | 7710560 |  |  | 64 | 6024.9 | 68225 |  | 165219 | 679326 | 468000 | 999.87 | 114943.75 | 18580.95 | 199029 | 39426 | 925970 |  | 60576 |  | 21454 | 1317728 |  | 38391 | 43702 | 9653 | 97122 |  | 1354 | 260547 | [5 empty] | 7305849.233 | 130 | 11400 | 4560
11 | 7711630 |  |  | 64 | 6032.3 | 68225 |  | 168824 | 682818 | 468000 | 999.87 | 116638.3 | 18741.48 | 199165 | 39551 | 926152 |  | 60601 |  | 21456 | 1317859 |  | 38409 | 43825 | 9659 | 97122 |  | 1364 | 260611 | [5 empty] | 7305849.233
12 | 7711810 |  |  | 64 | 6034 | 68225 |  | 171594 | 685344 | 468000 | 999.87 | 116638.3 | 18741.48 | 199165 | 39661 | 926181 |  | 60601 |  | 21456 | 1317975 |  | 38409 | 43828 | 9660 | 97122 |  | 1366 | 260611 | [5 empty] | 7305849.233
13 | 7711810 |  |  | 64 | 6034 | 68225 |  | 174035 | 687573 | 468000 | 999.87 | 116638.3 | 18741.48 | 199165 | 39661 | 926233 |  | 60601 |  | 21456 | 1317975 |  | 38409 | 43828 | 9660 | 97122 |  | 1366 | 260611 | [5 empty] | 7305849.233
14 | 7714250 |  |  | 64 | 6052 | 68225 |  | 177824 | 691043 | 468000 | 1042.47 | 117046.97 | 18822.18 | 199218 | 39841 | 926352 |  | 60759 |  | 21456 | 1318263 |  | 38448 | 43884 | 9669 | 97122 |  | 1373 | 260648 | [5 empty] | 7305849.233
15 | 7716630 |  |  | 64 | 6068.8 | 68225 |  | 181892 | 694776 | 468000 | 1065.31 | 118878.54 | 19190.88 | 199359 | 39970 | 926545 |  | 60830 |  | 21464 | 1318300 |  | 38458 | 43980 | 9684 | 97122 |  | 1395 | 260687 | [5 empty] | 7309868.532
16 | 7719410 |  |  | 64 | 6087.8 | 68225 |  | 186573 | 699076 | 468000 | 1065.31 | 121443.79 | 19529.35 | 199697 | 40067 | 926766 |  | 60993 |  | 21477 | 1318401 |  | 38515 | 44062 | 9700 | 97122 |  | 1420 | 260729 | [5 empty] | 7309920.592
17 | 7722070 |  |  | 64 | 6105.8 | 68225 |  | 191140 | 703265 | 468000 | 1080.34 | 125774.1 | 19894.68 | 200045 | 40251 | 926023 |  | 61145 |  | 21489 | 1318594 |  | 38547 | 44166 | 9718 | 97122 |  | 1450 | 260797 | [5 empty] | 7310001.764
18 | 7724350 |  |  | 64 | 6121.6 | 68225 |  | 195317 | 707092 | 468000 | 1130.64 | 130037.12 | 20213.94 | 200197 | 40390 | 927285 |  | 61253 |  | 21499 | 1318741 |  | 38630 | 44239 | 9731 | 97122 |  | 1471 | 260797 | [5 empty] | 7310001.764
19 | 7724600 |  |  | 64 | 6123.6 | 68225 |  | 198068 | 709612 | 468000 | 1130.64 | 130037.12 | 20213.94 | 200267 | 40434 | 927340 |  | 61258 |  | 21499 | 1318786 |  | 38630 | 44274 | 9732 | 97122 |  | 1472 | 260797 | [5 empty] | 7310001.764
20 | 7724600 |  |  | 64 | 6123.6 | 68225 |  | 200497 | 711836 | 468000 | 1130.64 | 130037.12 | 20213.94 | 200267 | 40434 | 927351 |  | 61258 |  | 21499 | 1318786 |  | 38630 | 44274 | 9732 | 97122 |  | 1472 | 260797 | [5 empty] | 7310001.764
21 | 7724850 |  |  | 64 | 6126.6 | 68225 |  | 202488 | 713632 | 468000 | 1130.64 | 130037.12 | 20213.94 | 200267 | 40434 | 927351 |  | 61258 |  | 21499 | 1318986 |  | 38630 | 44274 | 9732 | 97122 |  | 1472 | 260797 | [5 empty] | 7310001.764
22 | 7728800 |  |  | 64 | 6147.9 | 68225 |  | 207392 | 718157 | 468000 | 1166.65 | 131390.23 | 20458.5 | 200267 | 40607 | 927545 |  | 61424 |  | 21505 | 1318986 |  | 38666 | 44357 | 9749 | 97122 |  | 1489 | 260797 | [5 empty] | 7310001.764
23 | 7731870 |  |  | 64 | 6169.6 | 68225 |  | 211826 | 722231 | 468000 | 1261.9 | 134266.97 | 20956.43 | 200512 | 40774 | 927789 |  | 61575 |  | 21505 | 1319141 |  | 38706 | 44472 | 9762 | 97122 |  | 1519 | 260797 | [5 empty] | 7315729.638
24 | 7735330 |  |  | 64 | 6190.8 | 68225 |  | 216683 | 726692 | 468000 | 1349.77 | 136659.42 | 21416.23 | 200579 | 40997 | 928016 |  | 61789 |  | 21506 | 1319378 |  | 38728 | 44596 | 9777 | 97122 |  | 1550 | 260797 | [5 empty] | 7315736.573
25 | 7738290 |  |  | 64 | 6210.3 | 68225 |  | 221904 | 731486 | 468000 | 1522.95 | 138955.17 | 21755.66 | 200706 | 41294 | 928232 |  | 62040 |  | 21511 | 1319689 |  | 38766 | 44688 | 9789 | 97122 |  | 1576 | 260797 | [5 empty] | 7315739.602
26 | 7738290 |  |  | 64 | 6210.3 | 68225 |  | 224404 | 733764 | 468000 | 1522.95 | 138955.17 | 21755.66 | 200706 | 41294 | 928266 |  | 62040 |  | 21511 | 1319689 |  | 38766 | 44688 | 9789 | 97122 |  | 1576 | 260797 | [5 empty] | 7315739.602
27 | 7739050 |  |  | 64 | 6215.3 | 68225 |  | 227199 | 736325 | 468000 | 1522.95 | 138961.64 | 21757.17 | 200838 | 41294 | 928325 |  | 62044 |  | 21513 | 1319689 |  | 38766 | 44721 | 9789 | 97122 |  | 1576 | 260797 | [5 empty] | 7315739.602
28 | 7742570 |  |  | 64 | 6236.4 | 68225 |  | 232052 | 740786 | 468000 | 1780.57 | 141319.52 | 22207.03 | 201115 | 41404 | 928635 |  | 62236 |  | 21524 | 1319805 |  | 38842 | 44856 | 9824 | 97122 |  | 1608 | 260797 | [5 empty] | 7315739.602
29 | 7746550 |  |  | 64 | 6259.4 | 68225 |  | 237027 | 745358 | 468000 | 2244.47 | 144355.63 | 22667.72 | 201399 | 41535 | 928890 |  | 62437 |  | 21543 | 1319943 |  | 38874 | 44975 | 9858 | 97122 |  | 1639 | 260797 | [5 empty] | 7315739.602
30 | 7750170 |  |  | 64 | 6280.1 | 68225 |  | 241616 | 749572 | 468000 | 2575.84 | 146974.58 | 23034.83 | 201741 | 41678 | 929188 |  | 62611 |  | 21558 | 1320093 |  | 38925 | 45094 | 9892 | 97122 |  | 1667 | 260797 | [5 empty] | 7315739.602
31 | 7754140 |  |  | 64 | 6302.4 | 68225 |  | 246739 | 754278 | 468000 | 2685.77 | 150537.11 | 23841.23 | 201842 | 41916 | 929450 |  | 62815 |  | 21579 | 1320344 |  | 38971 | 45202 | 9926 | 97122 |  | 1698 | 260806 | [5 empty] | 7315747.721
1 | 7757140 |  |  | 64 | 6321.9 | 68225 |  | 250949 | 758148 | 468000 | 2762.8 | 152717.86 | 24152.66 | 202043 | 42122 | 929647 |  | 62984 |  | 21584 | 1320561 |  | 39028 | 45266 | 9949 | 97122 |  | 1715 | 260868 | [5 empty] | 7315747.721

## Utility Analysis October'25
GRENADA BREWERIES LIMITED
UTILITY ANALYSIS
MONTH: | [5 empty] | 2007-08-01
DATE |  |  | ELECTRICITY GRENLEC | CARIB GENSET | ELECTRICITY TOTAL | WATER | FUEL | CO2 | PRODUCTION - HL |  |  |  |  | UTILITY RATIOS
| METER 1 | METER 2 | [11 empty] | Elect | Water | Fuel | CO2
|  |  | USAGE (kwh) | USAGE (kwh) | USAGE (kwh) | USAGE (Hl) | USAGE (l) | USAGE (Kg.) | BREWED | BOTTLED | KEGS | OTHER | TOTAL | KWH/Hl | Hl/hl | Litres/hl | kg./Hl
1 | 5163 | 4732 | 9895 | 0 | 9895 | 4230 | 3570 | 2900 | 0 | 0 | 0 | 0 | 595.584 | 16.6139 | 7.1023 | 5.9941 | 4.8692
2 | 5155 | 4726 | 9881 | 0 | 9881 | 4880 | 3660 | 2400 | 0 | 0 | 0 | 0 | 649.968 | 15.2023 | 7.5081 | 5.631 | 3.6925
3 | 4942 | 4525 | 9467 | 0 | 9467 | 3460 | 3090 | 1600 | 0 | 0 | 0 | 0 | 295.482 | 32.0392 | 11.7097 | 10.4575 | 5.4149
4 | 2834 | 2528 | 5362 | 0 | 5362 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1876 | 1762 | 3638 | 0 | 3638 | 1240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 4863 | 4455 | 9318 | 0 | 9318 | 3470 | 3820 | 1700 | 0 | 0 | 0 | 0 | 257.004 | 36.2562 | 13.5017 | 14.8636 | 6.6147
7 | 4764 | 4366 | 9130 | 0 | 9130 | 3670 | 2810 | 1400 | 0 | 0 | 0 | 0 | 299.97 | 30.4364 | 12.2346 | 9.3676 | 4.6671
8 | 4776 | 4376 | 9152 | 0 | 9152 | 4370 | 3330 | 2200 | 0 | 0 | 0 | 0 | 408.408 | 22.409 | 10.7001 | 8.1536 | 5.3868
9 | 4301 | 3741 | 8042 | 0 | 8042 | 3930 | 2280 | 1163 | 0 | 0 | 0 | 0 | 197.208 | 40.7793 | 19.9282 | 11.5614 | 5.8973
10 | 3605 | 3492 | 7097 | 0 | 7097 | 2610 | 1070 | 1700 | 0 | 0 | 0 | 0 | 170.874 | 41.5335 | 15.2744 | 6.2619 | 9.9489
11 | 2770 | 2526 | 5296 | 0 | 5296 | 1100 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2441 | 2229 | 4670 | 0 | 4670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 3789 | 3470 | 7259 | 0 | 7259 | 2330 | 2440 | 800 | 0 | 0 | 0 | 0 | 64.944 | 111.7732 | 35.8771 | 37.5708 | 12.3183
14 | 4068 | 3733 | 7801 | 0 | 7801 | 2700 | 2380 | 1400 | 0 | 0 | 0 | 0 | 367.752 | 21.2127 | 7.3419 | 6.4718 | 3.8069
15 | 4681 | 4300 | 8981 | 0 | 8981 | 4350 | 2780 | 3100 | 0 | 0 | 0 | 0 | 338.778 | 26.51 | 12.8403 | 8.206 | 9.1505
16 | 4567 | 4189 | 8756 | 0 | 8756 | 5320 | 2660 | 3000 | 0 | 0 | 0 | 0 | 418.572 | 20.9187 | 12.7099 | 6.3549 | 7.1672
17 | 4177 | 3827 | 8004 | 0 | 8004 | 2910 | 2280 | 3500 | 0 | 0 | 0 | 0 | 350.724 | 22.8214 | 8.2971 | 6.5008 | 9.9794
18 | 2751 | 2520 | 5271 | 0 | 5271 | 1140 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 2429 | 2224 | 4653 | 0 | 4653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 1991 | 1796 | 3787 | 0 | 3787 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 4904 | 4525 | 9429 | 0 | 9429 | 1730 | 3950 | 1500 | 0 | 0 | 0 | 0 | 313.632 | 30.0639 | 5.516 | 12.5944 | 4.7827
22 | 4434 | 4074 | 8508 | 0 | 8508 | 4120 | 3070 | 2600 | 0 | 0 | 0 | 0 | 657.756 | 12.9349 | 6.2637 | 4.6674 | 3.9528
23 | 4857 | 4461 | 9318 | 0 | 9318 | 2900 | 3460 | 2200 | 0 | 0 | 0 | 0 | 685.872 | 13.5856 | 4.2282 | 5.0447 | 3.2076
24 | 5221 | 4794 | 10015 | 0 | 10015 | 4240 | 2960 | 2300 | 0 | 0 | 0 | 0 | 415.074 | 24.1282 | 10.215 | 7.1313 | 5.5412
25 | 2500 | 2278 | 4778 | 0 | 4778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 2795 | 2561 | 5356 | 0 | 5356 | 1320 | 760 | 0 | 0 | 0 | 0 | 0 | 18.15 | 295.0964 | 72.7273 | 41.8733 | 0
27 | 4853 | 4461 | 9314 | 0 | 9314 | 3870 | 3520 | 2200 | 0 | 0 | 0 | 0 | 571.164 | 16.3071 | 6.7756 | 6.1629 | 3.8518
28 | 4975 | 4572 | 9547 | 0 | 9547 | 4150 | 3980 | 3200 | 0 | 0 | 0 | 0 | 574.662 | 16.6132 | 7.2216 | 6.9258 | 5.5685
29 | 4589 | 4214 | 8803 | 0 | 8803 | 4850 | 3620 | 2500 | 0 | 0 | 0 | 0 | 570.018 | 15.4434 | 8.5085 | 6.3507 | 4.3858
30 | 5123 | 4706 | 9829 | 0 | 9829 | 3390 | 3970 | 2400 | 0 | 0 | 0 | 0 | 605.6904 | 16.2278 | 5.5969 | 6.5545 | 3.9624
31 | 4210 | 3870 | 8080 | 0 | 8080 | 4070 | 3000 | 1700 |  |  |  |  | 249.15 | 32.4303 | 16.3355 | 12.0409 | 6.8232
MTD
|  |  | Kwhr | Kwhr | Kwhr | Hl | L | kg. | hl | hl | hl | hl | hl | Elect | Water | Fuel | CO2
Total |  |  | 238437 | 0 | 238437 | 86700 | 69140 | 47463 | 0 | 0 | 0 | 0 | 9076.4364 | KWH/Hl | Hl/hl | Litres/hl | kg./Hl
[14 empty] | 26.2699 | 9.5522 | 7.6175 | 5.2293

## Steam Mass Flow
DATE | Steam Mass Flow Reading
1 | 0
2 | 0
3 | 0
4 | 121.094
5 | 0
6 | 137.246
7 | 0
8 | 0
9 | 0
10 | 0
11 | 0
12 | 0
13 | 0
14 | 4019.299
15 | 52.06
16 | 81.172
17 | 0
18 | 0
19 | 0
20 | 0
21 | 0
22 | 5727.874
23 | 6.935
24 | 3.029
25 | 0
26 | 0
27 | 0
28 | 0
29 | 0
30 | 8.119
31
10156.828

## Fuel
DAILY FUEL CONSUMPTION FOR OCTOBER 2025
DATE | Boiler 1 | Boiler 1 | Boiler 2 | Boiler 2 | Gen. | Gen | Boiler 1 sp. | Boiler 2 sp. | Gen. sp | Daily cons. | Total Prod.(HL) | Fuel(Litres/HL)
| Cons ( l ) | Hrs | Cons ( l ) | Hrs | Cons ( l ) | Hrs | cons (l/hr) | cons (l/hr) | Cons.(l/hr) | (litres)
1 | 3570 | 21.5 | 0 | 0 |  |  | 166.0465 | 0 | 0 | 3570 | 595.584 | 5.9941
2 | 3660 | 21 | 0 | 0 |  |  | 174.2857 | 0 | 0 | 3660 | 649.968 | 5.631
3 | 3090 | 18.3 | 0 | 0 |  |  | 168.8525 | 0 | 0 | 3090 | 295.482 | 10.4575
4 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
6 | 3820 | 23.7 | 0 | 0 |  |  | 161.1814 | 0 | 0 | 3820 | 257.004 | 14.8636
7 | 2810 | 18.3 | 0 | 0 |  |  | 153.5519 | 0 | 0 | 2810 | 299.97 | 9.3676
8 | 3330 | 20.53 | 0 | 0 |  |  | 162.2017 | 0 | 0 | 3330 | 408.408 | 8.1536
9 | 2280 | 15.67 | 0 | 0 |  |  | 145.501 | 0 | 0 | 2280 | 197.208 | 11.5614
10 | 1070 | 7.4 | 0 | 0 |  |  | 144.5946 | 0 | 0 | 1070 | 170.874 | 6.2619
11 | 180 | 1.7 | 0 | 0 |  |  | 105.8824 | 0 | 0 | 180 | 0 | 0
12 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
13 | 2440 | 18 | 0 | 0 |  |  | 135.5556 | 0 | 0 | 2440 | 64.944 | 37.5708
14 | 2380 | 16.8 | 0 | 0 |  |  | 141.6667 | 0 | 0 | 2380 | 367.752 | 6.4718
15 | 2780 | 19 | 0 | 0 |  |  | 146.3158 | 0 | 0 | 2780 | 338.778 | 8.206
16 | 2660 | 18 | 0 | 0 |  |  | 147.7778 | 0 | 0 | 2660 | 418.572 | 6.3549
17 | 2280 | 15.8 | 0 | 0 |  |  | 144.3038 | 0 | 0 | 2280 | 350.724 | 6.5008
18 | 250 | 2 | 0 | 0 |  |  | 125 | 0 | 0 | 250 | 0 | 0
19 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
20 | 250 | 3 | 0 | 0 |  |  | 83.3333 | 0 | 0 | 250 | 0 | 0
21 | 3950 | 21.3 | 0 | 0 |  |  | 185.446 | 0 | 0 | 3950 | 313.632 | 12.5944
22 | 3070 | 21.7 | 0 | 0 |  |  | 141.4747 | 0 | 0 | 3070 | 657.756 | 4.6674
23 | 3460 | 21.2 | 0 | 0 |  |  | 163.2075 | 0 | 0 | 3460 | 685.872 | 5.0447
24 | 2960 | 19.5 | 0 | 0 |  |  | 151.7949 | 0 | 0 | 2960 | 415.074 | 7.1313
25 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
26 | 760 | 5 | 0 | 0 |  |  | 152 | 0 | 0 | 760 | 18.15 | 41.8733
27 | 3520 | 21.1 | 0 | 0 |  |  | 166.8246 | 0 | 0 | 3520 | 571.164 | 6.1629
28 | 3980 | 23 | 0 | 0 |  |  | 173.0435 | 0 | 0 | 3980 | 574.662 | 6.9258
29 | 3620 | 20.7 |  | 0 |  |  | 174.8792 | 0 | 0 | 3620 | 570.018 | 6.3507
30 | 3970 | 22.3 |  | 0 |  |  | 178.0269 | 0 | 0 | 3970 | 605.6904 | 6.5545
31 | 3000 | 19.5 |  | 0 |  |  | 153.8462 | 0 | 0 | 3000 | 249.15
MTD | 69140 | 436 | 0 | 0 |  |  | 158.578 |  |  | 69140 | 9076.4364 | 7.6175 | 7.2 | 105.799
AVE. | 2659.2308 | 16.7692 |  |  |  |  | cons (l/hr)

## Water
| DATE | Well Supply (m3) | Nawasa Supply (m3) | Annanale Supply (m3) | RO Water Plant Nawasa (m3) | Service Water Received (m3) | Service Water Supply to Plant (m3) | CO2 Scrubber (m3) | Brewhouse / Old Pepsi Area (m3) | Filtration/Cellars (m3) | Cellars/Process Area (m3) | Pasteuriser (m3) |  |  |  |  | Permeate Produced (m3) | Plant Cons. USAGE (Hl.) |  | Bottle Filler (m3) |  |  | Rus (m3) | Washdown Area (m3) | TOTAL SUPPLY (M3) | Total Prod.(HL) | Water KPI (Hl/Hl)
[13 empty] | CIP Process (m3) | Bottles Washer (m3) | Bottles Filler (m3) | Boiler Supply (m3) |  |  | ∑ Service Water to Processes |  | Water into RO #1 (m3) | Water into RO #2 (m3)
-
| 1 | 0 | 232 | 191 | 200 | 223 | 287 | 0 | 261 | 0 | 0 | 12 | 52 | 119 | 32 | 21 | 0 | 2230 | 183 | 32 | 3 | 0 | 0 | 0 | 423 | 595.584 | 7.1023
| 2 | 0 | 251 | 237 | 250 | 238 | 294 | 0 | 204 | 0 | 0 | 23 | 58 | 118 | 0 | 19 | 0 | 2380 | 199 | 0 | 30 | 0 | 0 | 0 | 488 | 649.968 | 7.5081
| 3 | 0 | 148 | 198 | 208 | 138 | 206 | 0 | 223 | 0 | 0 | 11 | 39 | 74 | 49 | 17 | 0 | 1380 | 124 | 49 | 36 | 0 | 0 | 0 | 346 | 295.482 | 11.7097
| 4 | 0 | 10 | 25 | 26 | 9 | 67 | 0 | 3 | 0 | 0 | 0 | 0 | 38 | 3 | 7 | 0 | 90 | 38 | 3 | 0 | 0 | 0 | 0 | 35 | 0 | 0
| 5 | 0 | 27 | 97 | 102 | 22 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 220 | 5 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 0
| 6 | 0 | 219 | 128 | 134 | 213 | 211 | 0 | 303 | 0 | 0 | 15 | 55 | 66 | 16 | 24 | 0 | 2130 | 136 | 16 | 78 | 0 | 0 | 0 | 347 | 257.004 | 13.5017
| 7 | 0 | 116 | 251 | 264 | 103 | 216 | 0 | 222 | 0 | 0 | 10 | 44 | 81 | 17 | 13 | 0 | 1030 | 135 | 17 | 0 | 0 | 0 | 0 | 367 | 299.97 | 12.2346
| 8 | 0 | 234 | 203 | 214 | 223 | 252 | 0 | 248 | 0 | 0 | 11 | 60 | 96 | 19 | 17 | 0 | 2230 | 167 | 19 | 11 | 0 | 0 | 0 | 437 | 408.408 | 10.7001
| 9 | 0 | 207 | 186 | 194 | 199 | 165 | 0 | 215 | 0 | 0 | 3 | 34 | 60 | 10 | 12 | 0 | 1990 | 97 | 10 | 72 | 0 | 0 | 0 | 393 | 197.208 | 19.9282
| 10 | 0 | 136 | 125 | 131 | 130 | 182 | 0 | 25 | 0 | 0 | 2 | 18 | 123 | 10 | 6 | 0 | 1300 | 143 | 10 | 64 | 0 | 0 | 0 | 261 | 170.874 | 15.2744
| 11 | 0 | 0 | 110 | 116 | -6 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 1 | 0 | -60 | 3 | 2 | 0 | 0 | 0 | 0 | 110 | 0 | 0
| 12 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | 0 | 53 | 180 | 288 | -55 | 119 | 0 | 158 | 0 | 0 | 0 | 39 | 56 | 7 | 9 | 0 | -550 | 95 | 7 | 37 | 0 | 0 | 0 | 233 | 64.944 | 35.8771
| 14 | 0 | 141 | 129 | 37 | 233 | 193 | 0 | 71 | 0 | 0 | 8 | 10 | 96 | 22 | 15 | 0 | 2330 | 114 | 22 | 39 | 0 | 0 | 0 | 270 | 367.752 | 7.3419
| 15 | 0 | 338 | 97 | 101 | 334 | 221 | 0 | 163 | 0 | 0 | 13 | 57 | 82 | 25 | 16 | 0 | 3340 | 152 | 25 | 42 | 0 | 0 | 0 | 435 | 338.778 | 12.8403
| 16 | 0 | 348 | 184 | 193 | 339 | 0 | 0 | 152 | 0 | 0 | 12 | 32 | 104 | 30 | 18 | 0 | 3390 | 148 | 30 | 68 | 0 | 0 | 0 | 532 | 418.572 | 12.7099
| 17 | 0 | 152 | 139 | 147 | 144 | 1262 | 0 | 108 | 0 | 0 | 10 | 83 | 73 | 21 | 13 | 0 | 1440 | 166 | 21 | 0 | 0 | 0 | 0 | 291 | 350.724 | 8.2971
| 18 | 0 | 70 | 44 | 45 | 69 | 55 | 0 | 5 | 0 | 0 | 0 | 0 | 35 | 1 | 1 | 0 | 690 | 35 | 1 | 0 | 0 | 0 | 0 | 114 | 0 | 0
| 19 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 20 | 0 | 0 | 0 | 200 | -200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 21 | 0 | 0 | 173 | 0 | 173 | 194 | 0 | 166 | 0 | 0 | 6 | 36 | 83 | 17 | 17 | 0 | 1730 | 125 | 17 | 0 | 0 | 0 | 0 | 173 | 313.632 | 5.516
| 22 | 0 | 245 | 167 | 155 | 257 | 244 | 0 | 151 | 0 | 0 | 0 | 40 | 115 | 30 | 13 | 0 | 2570 | 155 | 30 | 0 | 0 | 0 | 0 | 412 | 657.756 | 6.2637
| 23 | 0 | 67 | 223 | 237 | 53 | 227 | 0 | 214 | 0 | 0 | 1 | 22 | 124 | 31 | 15 | 0 | 530 | 147 | 31 | 0 | 0 | 0 | 0 | 290 | 685.872 | 4.2282
| 24 | 0 | 127 | 297 | 311 | 113 | 216 | 0 | 251 | 0 | 0 | 5 | 38 | 92 | 26 | 12 | 0 | 1130 | 135 | 26 | 0 | 0 | 0 | 0 | 424 | 415.074 | 10.215
| 25 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 26 | 0 | 132 | 0 | 0 | 132 | 59 | 0 | 4 | 0 | 0 | 2 | 0 | 33 | 0 | 0 | 0 | 1320 | 35 | 0 | 0 | 0 | 0 | 0 | 132 | 18.15 | 72.7273
| 27 | 0 | 277 | 110 | 116 | 271 | 310 | 0 | 192 | 0 | 0 | 11 | 76 | 135 | 32 | 35 | 0 | 2710 | 222 | 32 | 0 | 0 | 0 | 0 | 387 | 571.164 | 6.7756
| 28 | 0 | 284 | 131 | 138 | 277 | 255 | 0 | 201 | 0 | 0 | 19 | 32 | 119 | 31 | 34 | 0 | 2770 | 170 | 31 | 0 | 0 | 0 | 0 | 415 | 574.662 | 7.2216
| 29 | 0 | 342 | 143 | 150 | 335 | 298 | 0 | 174 | 0 | 0 | 15 | 51 | 119 | 28 | 34 | 0 | 3350 | 185 | 28 | 0 | 0 | 0 | 0 | 485 | 570.018 | 8.5085
| 30 | 0 | 101 | 238 | 251 | 88 | 262 | 0 | 204 | 0 | 0 | 21 | 46 | 108 | 31 | 34 | 0 | 880 | 175 | 31 | 9 | 0 | 0 | 0 | 339 | 605.6904 | 5.5969
| 31 | 0 | 201 | 206 | 217 | 190 |  |  | 169 | 0 | 0 | 5 | 57 | 64 | 17 | 23 | 0 | 1900 |  | 17 | 62 | 0 | 0 | 0 | 407 | 249.15
MTD | total | 0 | 4458 | 4212 | 4425 | 4245 | 5927 |  | 4087 |  | 0 | 215 | 979 | 2221 | 507 | 426 | 0 | 42450 | 3289 | 507 | 551 |  |  |  | 8670 | 9076.4364 | 9.5522 | 10.2 | 93.6491
| Gals. |  | 980760
| NAWASA Cost/gal |  | 0.01581
| Proxy NAWASA water Cost |  | 15505.8156
| Add basic charge |  | 278.97
15784.7856
| Proxy sewage charge (2/3) |  | 10523.1904
| Proxy MTD NAWASA cost |  | 26307.976
Note on S4: Note: this is not truly accurate since this includes the service water reading on the inlet and not the outlet side (meters to be installed there)

## Elec.October'25
DAILY ELECTRICITY CONSUMPTION FOR OCTOBER 2025
DATE | Grenlec | In -house | Total Cons. (KW-HR) | Total Prod.(HL) | KPI. Elect (KW-H/Hl)
| In-feed (Kwhr) | Gen. (Kwhr)
1 | 9895 | 0 | 9895 | 595.584 | 16.6139
2 | 9881 | 0 | 9881 | 649.968 | 15.2023
3 | 9467 | 0 | 9467 | 295.482 | 32.0392
4 | 5362 | 0 | 5362 | 0 | 0
5 | 3638 | 0 | 3638 | 0 | 0
6 | 9318 | 0 | 9318 | 257.004 | 36.2562
7 | 9130 | 0 | 9130 | 299.97 | 30.4364
8 | 9152 | 0 | 9152 | 408.408 | 22.409
9 | 8042 | 0 | 8042 | 197.208 | 40.7793
10 | 7097 | 0 | 7097 | 170.874 | 41.5335
11 | 5296 | 0 | 5296 | 0 | 0
12 | 4670 | 0 | 4670 | 0 | 0
13 | 7259 | 0 | 7259 | 64.944 | 111.7732
14 | 7801 | 0 | 7801 | 367.752 | 21.2127
15 | 8981 | 0 | 8981 | 338.778 | 26.51
16 | 8756 | 0 | 8756 | 418.572 | 20.9187
17 | 8004 | 0 | 8004 | 350.724 | 22.8214
18 | 5271 | 0 | 5271 | 0 | 0
19 | 4653 | 0 | 4653 | 0 | 0
20 | 3787 | 0 | 3787 | 0 | 0
21 | 9429 | 0 | 9429 | 313.632 | 30.0639
22 | 8508 | 0 | 8508 | 657.756 | 12.9349
23 | 9318 | 0 | 9318 | 685.872 | 13.5856
24 | 10015 | 0 | 10015 | 415.074 | 24.1282
25 | 4778 | 0 | 4778 | 0 | 0
26 | 5356 | 0 | 5356 | 18.15 | 295.0964
27 | 9314 | 0 | 9314 | 571.164 | 16.3071
28 | 9547 | 0 | 9547 | 574.662 | 16.6132
29 | 8803 | 0 | 8803 | 570.018 | 15.4434
30 | 9829 | 0 | 9829 | 605.6904 | 16.2278
31 | 8080 |  | 8080 |  |  |  | %
MTD | 238437 | 0 | 238437 | 8827.2864 | 27.0114 | 22 | 122.7789
TARGET

## PROD.FIG.
PRODUCTION FOR OCTOBER 2025
DATE
| - | BOTTLED (Hl) | KEGS (Hl) | OTHER (Filtered) | Brewed | Transferred | TOTAL ( Hls)
Wednesday | 1 | [5 empty] | 595.584
Thursday | 2 | [5 empty] | 649.968
Friday | 3 | [5 empty] | 295.482
Saturday | 4 | [5 empty] | 0
Sunday | 5 | [5 empty] | 0
Monday | 6 | [5 empty] | 257.004
Tuesday | 7 | [5 empty] | 299.97
Wednesday | 8 | [5 empty] | 408.408
Thursday | 9 | [5 empty] | 197.208
Friday | 10 | [5 empty] | 170.874
Saturday | 11 | [5 empty] | 0
Sunday | 12 | [5 empty] | 0
Monday | 13 | [5 empty] | 64.944
Tuesday | 14 | [5 empty] | 367.752
Wednesday | 15 | [5 empty] | 338.778
Thursday | 16 | [5 empty] | 418.572
Friday | 17 | [5 empty] | 350.724
Saturday | 18 | [5 empty] | 0
Sunday | 19 | [5 empty] | 0
Monday | 20 | [5 empty] | 0
Tuesday | 21 | [5 empty] | 313.632
Wednesday | 22 | [5 empty] | 657.756
Thursday | 23 | [5 empty] | 685.872
Friday | 24 | [5 empty] | 415.074
Saturday | 25 | [5 empty] | 0
Sunday | 26 | [5 empty] | 18.15
Monday | 27 | [5 empty] | 571.164
Tuesday | 28 | [5 empty] | 574.662
Wednesday | 29 | [5 empty] | 570.018
Thursday | 30 | [5 empty] | 605.6904
Friday | 31 | [5 empty] | 249.15
[6 empty] | TOTAL | 9076.4364
0
Note on C4: Note: Unit of measurement

## CO2
CO2 Daily Consumption for OCTOBER 2025 | [7 empty] | TANK C
[6 empty] | FILLER |  | TAYLOR WHARTON CALIBRATION TANK | [5 empty] | NOT READY
DATE | FILLER Cons. (Kg.) | BMF Cons. (Kg.) | CO2 (kg.) (Ex. Vap'r Flowmeter) | CO2 (kg.) (Ex. Vap'r Calculation) | Total Prod.(HL) | CO2 ( Kg./HL) |  | inH2O | LBS_CO2 | KG_CO2 | READING Today (inH2O) |  |  | DATE | TANK C |  | TANK A | TANK B | INPUTS MOBILE(kg) | STOCK (KG) | TOTAL CONSUMPTION (KG)
[8 empty] | 10 | 722 | 327.4936 |  | POUNDS | KG |  | READING 00:30 hrs (inH2O) | QUANTITY (KG) | QUANTITY (KG) | QUANTITY (KG)
1 | 498.12 | 49.09 | 3160.48 | 2900 | 595.584 | 4.8692 |  | 20 | 2857 | 1295.9132 | 35 | 5243.5 | 2378.4112 | 2025-08-01 | 0 | 0 | #REF! | #REF! | #REF! | #REF!
2 | 521.42 | 84.01 | 3071.33 | 2400 | 649.968 | 3.6925 |  | 30 | 4344 | 1970.4049 |  |  |  | 2025-08-02 | 220 | 17467.8392 | 0 | 0 | 0 | 17467.8392 | 0
3 | 286.9 | 43.98 | 1724.6 | 1600 | 295.482 | 5.4149 |  | 40 | 6143 | 2786.4175 |  |  |  | 2025-08-03 | 220 | 17467.8392 | 0 | 0 | 0 | 17467.8392 | 2446.6768
4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50 | 7941 | 3601.9764 |  |  |  | 2025-08-04 | 190 | 15021.1623 | 0 | 0 | 0 | 15021.1623 | 15021.1623
5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 60 | 9739 | 4417.5353 |  |  |  | 2025-08-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 221.35 | 60.42 | 1940.55 | 1700 | 257.004 | 6.6147 |  | 70 | 11537 | 5233.0943 |  |  |  | 2025-08-06 | 0 | 0 | 0 | 0 | 0 | 0 | 12574.0319
7 | 242.73 | 41.02 | 1385.68 | 1400 | 299.97 | 4.6671 |  | 80 | 13335 | 6048.6532 |  |  |  | 2025-08-07 | 160 | 12574.0319 | 0 | 0 | 0 | 12574.0319
8 | 311.69 | 22.3 | 1739.31 | 2200 | 408.408 | 5.3868 |  | 90 | 15134 | 6864.6658 |  |  |  | 2025-08-08 | 140 | 10942.914 | 0 | 0 | 0 | 10942.914 | 0
9 | 171.58 | 0 | 1162.53 | 1163 | 197.208 | 5.8973 |  | 100 | 16932 | 7680.2247 |  |  |  | 2025-08-09 | 140 | 10942.914 | 0 | 0 | 19100 | 30042.914
10 | 160.53 | 0 | 1694.55 | 1700 | 170.874 | 9.9489 |  | 110 | 18730 | 8495.7836 |  |  |  | 2025-08-10 | 130 | 10126.9015 | 0 | 0 | 9967.237 | 20094.1385 | 4134.1385
11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 120 | 20528 | 9311.3426 |  |  |  | 2025-08-11 | 0 | 0 | 11400 | 4560 | 0 | 15960 | 15960
12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 130 | 22326 | 10126.9015 |  |  |  | 2025-08-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 80.7 | 42.6 | 408.67 | 800 | 64.944 | 12.3183 |  | 140 | 24125 | 10942.914 |  |  |  | 2025-08-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 368.7 | 22.84 | 1831.57 | 1400 | 367.752 | 3.8069 |  | 150 | 25923 | 11758.473 |  |  |  | 2025-08-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 338.47 | 0 | 2565.25 | 3100 | 338.778 | 9.1505 |  | 160 | 27721 | 12574.0319 |  |  |  | 2025-08-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 365.33 | 15.03 | 4330.31 | 3000 | 418.572 | 7.1672 |  | 170 | 29519 | 13389.5909 |  |  |  | 2025-08-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 319.26 | 50.3 | 4263.02 | 3500 | 350.724 | 9.9794 |  | 180 | 31317 | 14205.1498 |  |  |  | 2025-08-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 190 | 33116 | 15021.1623 |  |  |  | 2025-08-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 34914 | 15836.7213 |  |  |  | 2025-08-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 |  | 210 | 36712 | 16652.2802 |  |  |  | 2025-08-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 244.56 | 36.01 | 1353.11 | 1500 | 313.632 | 4.7827 |  | 220 | 38510 | 17467.8392 |  |  |  | 2025-08-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 497.93 | 95.25 | 2876.74 | 2600 | 657.756 | 3.9528 |  | 230 | 40308 | 18283.3981 |  |  |  | 2025-08-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 459.8 | 87.87 | 2392.45 | 2200 | 685.872 | 3.2076 |  | 240 | 42107 | 19099.4106 |  |  |  | 2025-08-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 339.43 | 173.18 | 2295.75 | 2300 | 415.074 | 5.5412 |  | 250 | 43905 | 19914.9696 |  |  |  | 2025-08-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 260 | 45703 | 20730.5285 |  |  |  | 2025-08-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 1.51 | 0 | 6.47 | 0 | 18.15 | 0 |  | 270 | 47501 | 21546.0875 |  |  |  | 2025-08-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 449.86 | 257.62 | 2357.88 | 2200 | 571.164 | 3.8518 |  | 280 | 49299 | 22361.6464 |  |  |  | 2025-08-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 460.69 | 463.9 | 3036.11 | 3200 | 574.662 | 5.5685 |  | 290 | 51098 | 23177.6589 |  |  |  | 2025-08-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 367.11 | 331.37 | 2618.95 | 2500 | 570.018 | 4.3858 |  | 300 | 52896 | 23993.2179 |  |  |  | 2025-08-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 806.4 | 109.93 | 3562.53 | 2400 | 605.6904 | 3.9624 |  | 310 | 54694 | 24808.7768 |  |  |  | 2025-08-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 311.43 | 77.03 | 2180.75 | 1700 | 249.15 | 6.8232 | TARGET | 320 | 56492 | 25624.3358 |  |  |  | 2025-08-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MTD | 7825.5 | 2063.75 | 51958.59 | 47463 | 9076.4364 | 5.2293 | 5 | 330 | 58290 | 26439.8947 |  |  |  | 2025-09-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 340 | 60089 | 27255.9072 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 350 | 60537 | 27459.1166 | [9 empty] | TOTAL | 50136.0096

## Daily KPIs CO2
Utilities Daily Consumption
1364
2025-10-01
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Monthly Target
Days | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Total |  | Diff.
Cases Produced |  | 9848 | 4477 | 0 | 0 | 3894 | 4545 | 6188 | 2988 | 2589 | 0 | 0 | 984 | 5572 | 5133 | 6342 | 5314 | 0 | 0 | 0 | 4752 | 9966 | 10392 | 6289 | 0 | 275 | 8654 | 8707 |  |  | 8361 | 115270 | 96325 | 18945
HL produced | 595.584 | 649.968 | 295.482 | 0 | 0 | 257.004 | 299.97 | 408.408 | 197.208 | 170.874 | 0 | 0 | 64.944 | 367.752 | 338.778 | 418.572 | 350.724 | 0 | 0 | 0 | 313.632 | 657.756 | 685.872 | 415.074 | 0 | 18.15 | 571.164 | 574.662 |  |  | 570.018 | 8221.596
Product Type | SSh/ST | SM/CB | CB/TING | 0 | 0 | TING/ST | CB/GN | GN/JC Cream | GN/JC Cream | JC Kola /JC Ging | 0 | 0 | JCSor | JC Sorr/ JC Gr\ST | ST/CBeP | Cbe P/Cbe R | Cbe R/CB | 0 | 0 | 0 | CB/ST | ST/CB | CB | CB/GN |  | Kegs | GN/ST/CB | CB/GN/ST |  |  | ST/VM
Water (m3)
Area | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | MTD
Well Supply (from filtered water) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nawasa Supply | 232 | 251 | 148 | 10 | 27 | 219 | 116 | 234 | 207 | 136 | 0 | 0 | 53 | 141 | 338 | 348 | 152 | 70 | 0 | 0 | 0 | 245 | 67 | 127 | 0 | 132 | 277 | 284 | 0 | 132 | 277 | 4223
Annanale Supply | 191 | 237 | 198 | 25 | 97 | 128 | 251 | 203 | 186 | 125 | 110 | 0 | 180 | 129 | 97 | 184 | 139 | 44 | 0 | 0 | 173 | 167 | 223 | 297 | 0 | 0 | 110 | 131 | 0 | 0 | 110 | 3735
Total Water Supply | 423 | 488 | 346 | 35 | 124 | 347 | 367 | 437 | 393 | 261 | 110 | 0 | 233 | 270 | 435 | 532 | 291 | 114 | 0 | 0 | 173 | 412 | 290 | 424 | 0 | 132 | 387 | 415 | 0 | 132 | 387 | 7958
0
Theoretical permeate | 146 | 182.5 | 151.84 | 18.98 | 74.46 | 97.82 | 192.72 | 156.22 | 141.62 | 95.63 | 84.68 | 0 | 210.24 | 210.24 | 210.24 | 210.24 | 210.24 | 210.24 | 0 | 146 | 0 | 113.15 | 173.01 | 227.03 | 0 | 0 | 0 | 0 | 0 | 0 | 109.5 | 3372.6 | 9472 |  | 11.5209
7.3
Permeate Produced | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Service Water Plant Supply | 287 | 294 | 206 | 67 | 6 | 211 | 216 | 252 | 165 | 182 | 29 | 52 | 119 | 193 | 221 | 0 | 1262 | 55 | 11 | 0 | 194 | 244 | 227 | 216 | 34 | 59 | 310 | 255 | 0 | 0 | 0 | 5367
Water consumption | 287 | 294 | 206 | 67 | 6 | 211 | 216 | 252 | 165 | 182 | 29 | 52 | 119 | 193 | 221 | 0 | 1262 | 55 | 11 | 0 | 194 | 244 | 227 | 216 | 34 | 59 | 310 | 255 | 0 | 0 | 0 | 5367
| 4.8188 | 4.5233 | 6.9717 |  |  | 8.21 | 7.2007 | 6.1703 | 8.3668 | 10.6511 |  |  | 18.3235 | 5.2481 | 6.5234 | 0 | 35.9827 |  |  |  | 6.1856 | 3.7096 | 3.3097 | 5.2039 |  | 32.5069 | 5.4275 | 4.4374 |  |  | 0
Water Consumption detail | [31 empty] | 0
Brewhouse / Old Pepsi Area | 261 | 204 | 223 | 3 | 0 | 303 | 222 | 248 | 215 | 25 | 0 | 0 | 158 | 71 | 163 | 152 | 108 | 5 | 0 | 0 | 166 | 151 | 214 | 251 | 0 | 4 | 192 | 201 | 0 | 4 | 192 | 3736
Spent Grains/Wash-down Areas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.7273 | 6.7756 | 79.5029
Whirlpool
Filtration/Cellars | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Processing/Cellars | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 12 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 115
CIP Process | 52 | 58 | 39 | 0 | 0 | 55 | 44 | 60 | 34 | 18 | 0 | 0 | 39 | 39 | 39 | 32 | 32 | 32 | 0 | 0 | 36 | 40 | 22 | 38 | 0 | 0 | 76 | 32 | 0 | 0 | 76 | 893 |  |  | 15588.1818
Bottles Washer | 119 | 118 | 74 | 38 | 5 | 66 | 81 | 96 | 60 | 123 | 3 | 0 | 56 | 56 | 56 | 56 | 56 | 56 | 0 | 0 | 83 | 115 | 124 | 92 | 0 | 33 | 135 | 119 | 0 | 33 | 135 | 1988
Bottle Filler | 32 | 0 | 49 | 3 | 0 | 16 | 17 | 19 | 10 | 10 | 2 | 0 | 7 | 22 | 25 | 30 | 21 | 1 | 0 | 0 | 17 | 30 | 31 | 26 | 0 | 0 | 32 | 31 | 0 | 0 | 32 | 463
Pasteuriser | 12 | 23 | 11 | 0 | 0 | 15 | 10 | 11 | 3 | 2 | 0 | 0 | 0 | 8 | 13 | 12 | 10 | 0 | 0 | 0 | 6 | 0 | 1 | 5 | 0 | 2 | 11 | 19 | 0 | 2 | 11 | 187
Boiler Supply | 21 | 19 | 17 | 7 | 0 | 24 | 13 | 17 | 12 | 6 | 1 | 0 | 9 | 9 | 16 | 18 | 18 | 1 | 0 | 0 | 17 | 13 | 15 | 12 | 0 | 0 | 35 | 34 | 0 | 0 | 35 | 369
Backwash Supply | [31 empty] | 0
Refrigeration Unit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CO2 Scrubber | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 11 | 38
Personnel Consumption
Total water consumption (M3) | 497 | 422 | 413 | 51 | 5 | 479 | 387 | 451 | 334 | 184 | 31 | 0 | 269 | 205 | 351 | 300 | 257 | 127 | 0 | 0 | 325 | 349 | 407 | 424 | 0 | 39 | 481 | 436 | 0 | 113.7273 | 530.7756 | 7868.5029
CO2 (kg.) (Tank Gauges)
CO2 (kg.) (Ex. Vap'r) | 3160.48 | 3071.33 | 1724.6 | 0 | 0 | 1940.55 | 1385.68 | 1739.31 | 1162.53 | 1694.55 | 0 | 0 | 408.67 | 1831.57 | 2565.25 | 4330.31 | 4263.02 | 319.26 | 152 | 139 | 70 | 44 | 55 | 0 | 5 | 0 | 0 | 45 | 0 | 0 | 35 | 30142.11
CO2 (kg.) (Filler) | 498.12 | 521.42 | 286.9 | 0 | 0 | 221.35 | 242.73 | 311.69 | 171.58 | 160.53 | 0 | 0 | 80.7 | 368.7 | 338.47 | 365.33 | 319.26 | 0 | 0 | 0 | 244.56 | 497.93 | 459.8 | 339.43 | 0 | 1.51 | 449.86 | 460.69 | 367.11 | 806.4 | 311.43 | 7825.5
Electricity (Kwh.) | 9895 | 9881 | 9467 | 5362 | 3638 | 9318 | 9130 | 9152 | 8042 | 7097 | 5296 | 4670 | 7259 | 7801 | 8981 | 8756 | 8004 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 189730
Fuel (L) | 3570 | 3660 | 3090 | 0 | 0 | 3820 | 2810 | 3330 | 2280 | 1070 | 180 | 0 | 2440 | 2380 | 2780 | 2660 | 2280 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 39850
Water (m3)
Area | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 9 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | MTD | Target | Diff
Total water consumption | 7.1023 | 7.5081 | 11.7097 |  |  | 13.5017 | 12.2346 | 10.7001 | 19.9282 | 15.2744 |  |  | 35.8771 | 7.3419 | 12.8403 | 12.7099 | 8.2971 |  |  |  | 5.516 | 6.2637 | 4.2282 | 10.215 |  | 72.7273 | 6.7756 | 7.2216 |  |  | 6.7893 | 9.6794 | 10.2 | 0.52061
Consumption detail | [31 empty] | MTD | Target | Diff
Brewhouse / Old Pepsi Area | 4.3823 | 3.1386 | 7.547 |  |  | 11.7897 | 7.4007 | 6.0724 | 10.9022 | 1.4631 |  |  | 24.3287 | 1.9306 | 4.8114 | 3.6314 | 3.0793 |  |  |  | 5.2928 | 2.2957 | 3.1201 | 6.0471 |  | 2.2039 | 3.3616 | 3.4977 |  |  | 3.3683 | 4.5441 | 2.5 | -2.0441
Brewhouse (Hls brewed) | Wed: 5.1622; Thu: 4.5404; Fri: 7.6057; Mon: 5.8124; Tue: 4.8567; Wed: 4.5083; Thu: 7.0794; Mon: 3.8754; Fri: 5.5046; Tue: 3.8126; Wed: 3.7183; Thu: 5.4999; Fri: 5.4601; Mon: 4.7013; Tue: 3.6712; Wed: 0; Thu: 0.088711; Fri: 4.3224 | 4.8711 | 2.5 | -2.3711
Spent Grains/Wash-down Areas | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  | 0.11887 | 0.0967 | 0.1 | 0.0032999
Whirlpool | [32 empty] | 0.1 | 0.1
Filtration/Cellars | Wed: 0; Thu: 0; Fri: 0; Mon: 0; Tue: 0; Wed: 0; Thu: 0; Fri: 0; Mon: 0; Tue: 0; Wed: 0; Thu: 0; Fri: 0; Tue: 0 | 0 | 0.7 | 0.7
Processing/Cellars | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 1.1512 | 0 | 0.34215 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  | 0.56139 | 0.13988 | 1 | 0.86012
CIP Process | 0.87309 | 0.89235 | 1.3199 |  |  | 2.14 | 1.4668 | 1.4691 | 1.7241 | 1.0534 |  |  | 6.0052 | 1.0605 | 1.1512 | 0.7645 | 0.9124 |  |  |  | 1.1478 | 0.60813 | 0.32076 | 0.9155 |  | 0 | 1.3306 | 0.55685 |  |  | 1.3333 | 1.0862 | 0.7 | -0.38616
Bottles Washer | 1.998 | 1.8155 | 2.5044 |  |  | 2.5681 | 2.7003 | 2.3506 | 3.0425 | 7.1983 |  |  | 8.6228 | 1.5228 | 1.653 | 1.3379 | 1.5967 |  |  |  | 2.6464 | 1.7484 | 1.8079 | 2.2165 |  | 18.1818 | 2.3636 | 2.0708 |  |  | 2.3683 | 2.418 | 2.6 | 0.18198
Bottle Washer | [32 empty] | 2.6 | 2.6
Bottle Filler | 0.53729 | 0 | 1.6583 |  |  | 0.62256 | 0.56672 | 0.46522 | 0.50708 | 0.58523 |  |  | 1.0779 | 0.59823 | 0.73795 | 0.71672 | 0.59876 |  |  |  | 0.54204 | 0.4561 | 0.45198 | 0.62639 |  | 0 | 0.56026 | 0.53945 |  |  | 0.56139 | 0.56315 | 0.7 | 0.13685
Pasteuriser | 0.20148 | 0.35386 | 0.37227 |  |  | 0.58365 | 0.33337 | 0.26934 | 0.15212 | 0.11705 |  |  | 0 | 0.21754 | 0.38373 | 0.28669 | 0.28512 |  |  |  | 0.19131 | 0 | 0.01458 | 0.12046 |  | 1.1019 | 0.19259 | 0.33063 |  |  | 0.19298 | 0.22745 | 0.1 | -0.12745
Boiler Supply | 0.3526 | 0.29232 | 0.57533 |  |  | 0.93384 | 0.43338 | 0.41625 | 0.60849 | 0.35114 |  |  | 1.3858 | 0.24473 | 0.47229 | 0.43003 | 0.51322 |  |  |  | 0.54204 | 0.19764 | 0.2187 | 0.28911 |  | 0 | 0.61278 | 0.59165 |  |  | 0.61402 | 0.44882 | 0.6 | 0.15118
Backwash Supply | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0.5 | 0.5
Refrigeration Unit | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0.3 | 0.3
CO2 Scrubber | [32 empty] | 0.4 | 0.4
Personnel Consumption | [32 empty] | 0.2 | 0.2
Water consumption (M3) | 13.5069 | 11.033 | 21.5829 | 0 | 0 | 24.4502 | 17.758 | 15.5511 | 24.0158 | 10.7682 | 0 | 0 | 45.2957 | 5.5744 | 10.3608 | 7.1672 | 12.8323 | 0 | 0 | 0 | 14.175 | 9.0242 | 11.4339 | 15.6751 | 0 | 21.4876 | 13.1227 | 11.2583 | 0 | 0.088711 | 13.441 | 14.3954 | 15.6 | 1.2046
Bottling Hall water | 2.7368 | 2.1693 | 4.535 | 0 | 0 | 3.7743 | 3.6004 | 3.0852 | 3.7017 | 7.9006 | 0 | 0 | 9.7007 | 2.3385 | 2.7747 | 2.3413 | 2.4806 | 0 | 0 | 0 | 3.3798 | 2.2045 | 2.2745 | 2.9633 | 0 | 19.2837 | 3.1164 | 2.9409 | 0 | 0 | 3.1227 | 3.2086 | 6 | 2.7914
CO2 (kg./Hl.) KPI | 5.3065 | 4.7254 | 5.8366 |  |  | 7.5507 | 4.6194 | 4.2588 | 5.8949 | 9.917 |  |  | 6.2927 | 4.9804 | 7.5721 | 10.3454 | 12.1549 |  |  |  | 0.22319 | 0.066894 | 0.08019 | 0 |  | 0 | 0 | 0.078307 |  |  | 0.061402 | 3.6662 | 5 | 1.3338
CO2 Filler (kg./Hl.) KPI | 0.83636 | 0.80222 | 0.97096 |  |  | 0.86127 | 0.80918 | 0.76318 | 0.87005 | 0.93946 |  |  | 1.2426 | 1.0026 | 0.99909 | 0.8728 | 0.91029 |  |  |  | 0.77977 | 0.75701 | 0.67039 | 0.81776 |  | 0.083196 | 0.78762 | 0.80167 |  |  | 0.54635 | 0.95182 | 1.7 | 0.74818
Electricity (Kwh./Hl.) KPI | 16.6139 | 15.2023 | 32.0392 |  |  | 36.2562 | 30.4364 | 22.409 | 40.7793 | 41.5335 |  |  | 111.7732 | 21.2127 | 26.51 | 20.9187 | 22.8214 |  |  |  | 16.8063 | 8.0136 | 7.6851 | 12.6989 |  | 290.4132 | 9.2285 | 9.1723 |  |  | 9.2471 | 23.077 | 22 | -1.077
[33 empty] | 31.2 | 31.2
Fuel (L/Hl.) KPI | 5.9941 | 5.631 | 10.4575 |  |  | 14.8636 | 9.3676 | 8.1536 | 11.5614 | 6.2619 |  |  | 37.5708 | 6.4718 | 8.206 | 6.3549 | 6.5008 |  |  |  | 0.79711 | 0.38008 | 0.3645 | 0.6023 |  | 13.7741 | 0.4377 | 0.43504 |  |  | 0.43858 | 4.847 | 7.2 | 2.353
Total Bottles Washed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | .
CO2 to Liqufier (kg.) | 49.09 | 84.01 | 43.98 | 0 | 0 | 60.42 | 41.02 | 22.3 | 0 | 0 | 0 | 0 | 42.6 | 22.84 | 0 | 15.03 | 50.3 | 0 | 0 | 0 | 36.01 | 95.25 | 87.87 | 173.18 | 0 | 0 | 257.62 | 463.9 | 331.37 | 109.93 | 77.03 | 2063.75
CO2 recovered (Kg - liquid) | [31 empty] | 0
CO2 liquid conversion efficiency | [31 empty] | 0% | bar: Wed to Fri; Mon to Wed; Mon to Tue; Thu to Fri; Tue to Fri; Mon to Fri
Water Recovered (m3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tanks on Collection
Hls Brewed | 505.6 | 449.3 | 293.2 | 0 | 0 | 521.3 | 457.1 | 550.1 | 303.7 | 0 | 0 | 0 | 407.7 | 0 | 0 | 0 | 196.2 | 0 | 0 | 0 | 435.4 | 406.1 | 389.1 | 459.7 | 0 | 0 | 408.4 | 547.5 | 444.2 | 450.9 | 444.2 | 7669.7
Product | CB | CB/ST | ST | 0 | 0 | TING/ST | CB/ST | ST | CB | 0 | 0 | 0 | GU | 0 | 0 | 0 | ST | 0 | 0 | 0 | ST/CB | CB | VM | CB | 0 | 0 | CB | CB/ ST | ST/CB | CB/ST/GU | ST/CB
No. of Brews | 10 | 9 | 6 | 0 | 0 | 10 | 9 | 11 | 6 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 9 | 8 | 8 | 9 | 0 | 0 | 8 | 11 | 9 | 9 | 9 | 153
Raw Water In - Nawasa | 200 | 250 | 208 | 26 | 102 | 134 | 264 | 214 | 194 | 131 | 116 | 0 | 288 | 288 | 288 | 288 | 288 | 288 | 0 | 200 | 0 | 155 | 237 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 4620
Into RO | [31 empty] | 0 | bar: Wed
| 9895 | 9881 | 9467 | 5362 | 3638 | 9318 | 9130 | 9152 | 8042 | 7097 | 5296 | 4670 | 7259 | 7801 | 8981 | 8756 | 8004 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 5271 | 189730
Note on A79: RAntoine: Line deleted by MD on April 20, 2011. Do not reinsert

## Daily KPIs
Utilities Daily Consumption
1904-12-04
2025-10-02 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  |  | Monthly Target
| Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri |  | Total |  | Diff.
Cases Produced | 9024 | 9848 | 4477 |  |  | 3894 | 4545 | 6188 | 2988 | 2589 |  |  | 984 | 5572 | 5133 | 6342 | 5314 |  |  |  | 4752 | 9966 | 10392 | 6289 |  | 275 | 8654 | 8707 | 8361 | 8666 | 3775 |  | 136735 | 102700 | 34035
HL produced | 595.584 | 649.968 | 295.482 |  |  | 257.004 | 299.97 | 408.408 | 197.208 | 170.874 |  |  | 64.944 | 367.752 | 338.778 | 418.572 | 350.724 |  |  |  | 313.632 | 657.756 | 685.872 | 415.074 | 0 | 18.15 | 571.164 | 574.662 | 570.018 | 605.6904 | 249.15 |  | 9076.4364
Product Type | SSh/ST | SM/CB | CB/TING |  |  | TING/ST | ST/CB | CB/GN | GN/JC Cream | JC Kola /JC Ging |  |  | JCSor | JC Sorr/ JC Gr\ST | ST/CBeP | Cbe P/Cbe R | Cbe R/CB |  |  |  | CB/ST | ST/CB | CB | CB/GN |  | Kegs | GN/ST/CB | CB/GN/ST | ST/VM | VM/CB | CB/GO
Hls Brewed | Wed: 505.6; Thu: 449.3; Fri: 293.2; Mon: 521.3; Tue: 457.1; Wed: 550.1; Thu: 303.7; Mon: 407.7; Fri: 196.2; Tue: 435.4; Wed: 406.1; Thu: 389.1; Fri: 459.7; Mon: 408.4; Tue: 547.5; Wed: 444.2; Thu: 450.9; Fri: 354.5 |  | 7580
Product | Wed: CB; Thu: CB/ST; Fri: ST; Mon: CB; Tue: CB/ST; Wed: ST; Thu: CB; Mon: GU; Fri: ST; Tue: ST/CB; Wed: CB; Thu: VM; Fri: CB; Mon: CB; Tue: CB/ ST; Wed: ST/CB; Thu: CB/ST/GU; Fri: GU
No. of Brews | Wed: 10; Thu: 9; Fri: 6; Mon: 10; Tue: 9; Wed: 11; Thu: 6; Mon: 8; Fri: 4; Tue: 9; Wed: 8; Thu: 8; Fri: 9; Mon: 8; Tue: 11; Wed: 9; Thu: 9; Fri: 7 |  | 151
Brewhouse (Hls brewed) | Wed: 5.1622; Thu: 4.5404; Fri: 7.6057; Mon: 5.8124; Tue: 4.8567; Wed: 4.5083; Thu: 7.0794; Mon: 3.8754; Fri: 5.5046; Tue: 3.8126; Wed: 3.7183; Thu: 5.4999; Fri: 5.4601; Mon: 4.7013; Tue: 3.6712; Wed: 3.9172; Thu: 4.5243; Fri: 4.7673 |  | 5.3918
Water (m3)
MTD
Well Supply (from filtered water) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Nawasa Supply | 232 | 251 | 148 | 10 | 27 | 219 | 116 | 234 | 207 | 136 | 0 | 0 | 53 | 141 | 338 | 348 | 152 | 70 | 0 | 0 | 0 | 245 | 67 | 127 | 0 | 132 | 277 | 284 | 342 | 101 | 201 |  | 4458
Annanale Supply | 191 | 237 | 198 | 25 | 97 | 128 | 251 | 203 | 186 | 125 | 110 | 0 | 180 | 129 | 97 | 184 | 139 | 44 | 0 | 0 | 173 | 167 | 223 | 297 | 0 | 0 | 110 | 131 | 143 | 238 | 206 |  | 4212
Total Water Supply | 423 | 488 | 346 | 35 | 124 | 347 | 367 | 437 | 393 | 261 | 110 | 0 | 233 | 270 | 435 | 532 | 291 | 114 | 0 | 0 | 173 | 412 | 290 | 424 | 0 | 132 | 387 | 415 | 485 | 339 | 407 |  | 8670
0
Theoretical permeate | 146 | 182.5 | 151.84 | 18.98 | 74.46 | 97.82 | 192.72 | 156.22 | 141.62 | 95.63 | 84.68 | 0 | 210.24 | 27.01 | 73.73 | 140.89 | 107.31 | 32.85 | 0 | 146 | 0 | 113.15 | 173.01 | 227.03 | 0 | 0 | 84.68 | 100.74 | 109.5 | 183.23 | 158.41 |  | 3230.25 | 10440 |  | 11.5023
7.3
Permeate Produced | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Service Water Plant Supply | 287 | 294 | 206 | 67 | 6 | 211 | 216 | 252 | 165 | 182 | 29 | 52 | 119 | 193 | 221 | 0 | 1262 | 55 | 11 | 0 | 194 | 244 | 227 | 216 | 34 | 59 | 310 | 255 | 298 | 262 | 0 |  | 5927
Brewhouse | 261 | 204 | 223 | 3 | 0 | 303 | 222 | 248 | 215 | 25 | 0 | 0 | 158 | 71 | 163 | 152 | 108 | 5 | 0 | 0 | 166 | 151 | 214 | 251 | 0 | 4 | 192 | 201 | 174 | 204 | 169 |  | 4087
Boiler Supply | 21 | 19 | 17 | 7 | 0 | 24 | 13 | 17 | 12 | 6 | 1 | 0 | 9 | 15 | 16 | 18 | 13 | 1 | 0 | 0 | 17 | 13 | 15 | 12 | 0 | 0 | 35 | 34 | 34 | 34 | 23 |  | 426
Water consumption | 569 | 517 | 446 | 77 | 6 | 538 | 451 | 517 | 392 | 213 | 30 | 52 | 286 | 279 | 400 | 170 | 1383 | 61 | 11 | 0 | 377 | 408 | 456 | 479 | 34 | 63 | 537 | 490 | 506 | 500 | 192 |  | 10440
Water Consumption detail
Brewhouse | 261 | 204 | 223 | 3 | 0 | 303 | 222 | 248 | 215 | 25 | 0 | 0 | 158 | 71 | 163 | 152 | 108 | 5 | 0 | 0 | 166 | 151 | 214 | 251 | 0 | 4 | 192 | 201 | 174 | 204 | 169 |  | 4087
Spent grains/wash-down area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 485 |  | 485
Whirlpool
Cellars/Filtration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Processing/Cellars | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
CIP Process | 52 | 58 | 39 | 0 | 0 | 55 | 44 | 60 | 34 | 18 | 0 | 0 | 39 | 10 | 57 | 32 | 83 | 0 | 0 | 0 | 36 | 40 | 22 | 38 | 0 | 0 | 76 | 32 | 51 | 46 | 57 |  | 979
Bottles Washer | 119 | 118 | 74 | 38 | 5 | 66 | 81 | 96 | 60 | 123 | 3 | 0 | 56 | 96 | 82 | 104 | 73 | 35 | 0 | 0 | 83 | 115 | 124 | 92 | 0 | 33 | 135 | 119 | 119 | 108 | 64 |  | 2221
Bottle Filler | 32 | 0 | 49 | 3 | 0 | 16 | 17 | 19 | 10 | 10 | 2 | 0 | 7 | 22 | 25 | 30 | 21 | 1 | 0 | 0 | 17 | 30 | 31 | 26 | 0 | 0 | 32 | 31 | 28 | 31 | 17 |  | 507
Pasteuriser | 12 | 23 | 11 | 0 | 0 | 15 | 10 | 11 | 3 | 2 | 0 | 0 | 0 | 8 | 13 | 12 | 10 | 0 | 0 | 0 | 6 | 0 | 1 | 5 | 0 | 2 | 11 | 19 | 15 | 21 | 5 |  | 215
Boiler Supply | 21 | 19 | 17 | 7 | 0 | 24 | 13 | 17 | 12 | 6 | 1 | 0 | 9 | 15 | 16 | 18 | 13 | 1 | 0 | 0 | 17 | 13 | 15 | 12 | 0 | 0 | 35 | 34 | 34 | 34 | 23 |  | 426
Refrigeration Unit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
CO2 Scrubber | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Personnel Consumption
Backwash Supply | [32 empty] | 0
Total water consumption (M3) | 497 | 422 | 413 | 51 | 5 | 479 | 387 | 451 | 334 | 184 | 6 | 0 | 269 | 222 | 356 | 348 | 308 | 42 | 0 | 0 | 325 | 349 | 407 | 424 | 0 | 39 | 481 | 436 | 421 | 444 | 820 |  | 8920
Consumption detail | [32 empty] | MTD | Target | Diff
Brewhouse/Filtration/Cellar | 4.3823 | 3.1386 | 7.547 |  |  | 11.7897 | 7.4007 | 6.0724 | 10.9022 | 1.4631 |  |  | 24.3287 | 1.9306 | 4.8114 | 3.6314 | 3.0793 |  |  |  | 5.2928 | 2.2957 | 3.1201 | 6.0471 |  | 2.2039 | 3.3616 | 3.4977 | 3.0525 | 3.3681 | 6.7831 |  | 4.5029 | 3.2 | -1.3029
Spent Grains/Wash-down Areas | [32 empty] | 0.53435 | 0.1 | -0.43435
Whirlpool | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0.1 | 0.1
Cellars/Filtration | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0.7 | 0.7
Processing/Cellars | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1 | 1
CIP Process | 0.87309 | 0.89235 | 1.3199 |  |  | 2.14 | 1.4668 | 1.4691 | 1.7241 | 1.0534 |  |  | 6.0052 | 0.27192 | 1.6825 | 0.7645 | 2.3665 |  |  |  | 1.1478 | 0.60813 | 0.32076 | 0.9155 |  | 0 | 1.3306 | 0.55685 | 0.89471 | 0.75946 | 2.2878 |  | 1.0786 | 0.7 | -0.37862
Bottles Washer | 1.998 | 1.8155 | 2.5044 |  |  | 2.5681 | 2.7003 | 2.3506 | 3.0425 | 7.1983 |  |  | 8.6228 | 2.6105 | 2.4205 | 2.4846 | 2.0814 |  |  |  | 2.6464 | 1.7484 | 1.8079 | 2.2165 |  | 18.1818 | 2.3636 | 2.0708 | 2.0877 | 1.7831 | 2.5687 |  | 2.447 | 2.1 | -0.347
Bottle Filler | 0.53729 | 0 | 1.6583 |  |  | 0.62256 | 0.56672 | 0.46522 | 0.50708 | 0.58523 |  |  | 1.0779 | 0.59823 | 0.73795 | 0.71672 | 0.59876 |  |  |  | 0.54204 | 0.4561 | 0.45198 | 0.62639 |  | 0 | 0.56026 | 0.53945 | 0.49121 | 0.51181 | 0.68232 |  | 0.55859 | 0.7 | 0.14141
Pasteuriser | 0.20148 | 0.35386 | 0.37227 |  |  | 0.58365 | 0.33337 | 0.26934 | 0.15212 | 0.11705 |  |  | 0 | 0.21754 | 0.38373 | 0.28669 | 0.28512 |  |  |  | 0.19131 | 0 | 0.01458 | 0.12046 |  | 1.1019 | 0.19259 | 0.33063 | 0.26315 | 0.34671 | 0.20068 |  | 0.23688 | 0.1 | -0.13688
Boiler Supply | 0.3526 | 0.29232 | 0.57533 |  |  | 0.93384 | 0.43338 | 0.41625 | 0.60849 | 0.35114 |  |  | 1.3858 | 0.40788 | 0.47229 | 0.43003 | 0.37066 |  |  |  | 0.54204 | 0.19764 | 0.2187 | 0.28911 |  | 0 | 0.61278 | 0.59165 | 0.59647 | 0.56134 | 0.92314 |  | 0.46935 | 0.6 | 0.13065
Backwash Supply | [33 empty] | 0.5 | 0.5
Refrigeration Unit | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0.3 | 0.3
CO2 Scrubber | [33 empty] | 0.4 | 0.4
Personnel Consumption | [33 empty] | 0.2 | 0.2
Water consumption (M3) | 8.3448 | 6.4926 | 13.9772 | 0 | 0 | 18.6378 | 12.9013 | 11.0429 | 16.9364 | 10.7682 | 0 | 0 | 41.4203 | 6.0367 | 10.5084 | 8.314 | 8.7818 | 0 | 0 | 0 | 10.3625 | 5.3059 | 5.9341 | 10.215 | 0 | 21.4876 | 8.4214 | 7.5871 | 7.3857 | 7.3305 | 13.4457 |  | 9.8276 | 9.6 | -0.22765
Bottling Hall water | 2.7368 | 2.1693 | 4.535 | 0 | 0 | 3.7743 | 3.6004 | 3.0852 | 3.7017 | 7.9006 | 0 | 0 | 9.7007 | 3.4262 | 3.5421 | 3.488 | 2.9653 | 0 | 0 | 0 | 3.3798 | 2.2045 | 2.2745 | 2.9633 | 0 | 19.2837 | 3.1164 | 2.9409 | 2.842 | 2.6416 | 3.4517 |  | 3.2425 | 2.9 | -0.34246
Water Plant Total (Before Sand Filter) | 200 | 250 | 208 | 26 | 102 | 134 | 264 | 214 | 194 | 131 | 116 | 0 | 288 | 37 | 101 | 193 | 147 | 45 | 0 | 200 | 0 | 155 | 237 | 311 | 0 | 0 | 116 | 138 | 150 | 251 | 217 |  | 4425
CO2 (kg.) Filler | [32 empty] | 0
CO2 (kg.) (Ex. Vap'r) | 2900 | 2400 | 1600 | 0 | 0 | 1700 | 1400 | 2200 | 1163 | 1700 | 0 | 0 | 800 | 1400 | 3100 | 3000 | 3500 | 0 |  |  | 1500 | 2600 | 2200 | 2300 | 0 | 0 | 2200 | 3200 | 2500 | 2400 | 1700 | 0 | 47463
CO2 (Totalizer Meter) | 3160.48 | 3071.33 | 1724.6 | 0 | 0 | 1940.55 | 1385.68 | 1739.31 | 1162.53 | 1694.55 | 0 | 0 | 408.67 | 1831.57 | 2565.25 | 4330.31 | 4263.02 | 0 | 0 | 0 | 1353.11 | 2876.74 | 2392.45 | 2295.75 | 0 | 6.47 | 2357.88 | 3036.11 | 2618.95 | 3562.53 | 2180.75 |  | 51958.59
CO2 (kg.) (Filler) | 498.12 | 521.42 | 286.9 | 0 | 0 | 221.35 | 242.73 | 311.69 | 171.58 | 160.53 | 0 | 0 | 80.7 | 368.7 | 338.47 | 365.33 | 319.26 | 0 | 0 | 0 | 244.56 | 497.93 | 459.8 | 339.43 | 0 | 1.51 | 449.86 | 460.69 | 367.11 | 806.4 | 311.43 |  | 7825.5
CO2 (kg.) (BMF) | 49.09 | 84.01 | 43.98 | 0 | 0 | 60.42 | 41.02 | 22.3 | 0 | 0 | 0 | 0 | 42.6 | 22.84 | 0 | 15.03 | 50.3 | 0 | 0 | 0 | 36.01 | 95.25 | 87.87 | 173.18 | 0 | 0 | 257.62 | 463.9 | 331.37 | 109.93 | 77.03 |  | 2063.75
0
CO2 (kg.)Consumption Meter | 3160.48 | 3071.33 | 1724.6 | 0 | 0 | 1940.55 | 1385.68 | 1739.31 | 1162.53 | 1694.55 |  | 0 |  | 1831.57 | 2565.25 | 4330.31 | 4263.02 | 319.26 | 152 | 139 | 70 | 44 | 55 | 0 | 5 | 0 | 0 | 45 | 35 | 30142.11 | 0
Electricity (Kwh.) | 9895 | 9881 | 9467 | 5362 | 3638 | 9318 | 9130 | 9152 | 8042 | 7097 | 5296 | 4670 | 7259 | 7801 | 8981 | 8756 | 8004 | 5271 | 4653 | 3787 | 9429 | 8508 | 9318 | 10015 | 4778 | 5356 | 9314 | 9547 | 8803 | 9829 | 8080 |  | 238437
Fuel (L) | 3570 | 3660 | 3090 | 0 | 0 | 3820 | 2810 | 3330 | 2280 | 1070 | 180 | 0 | 2440 | 2380 | 2780 | 2660 | 2280 | 250 | 0 | 250 | 3950 | 3070 | 3460 | 2960 | 0 | 760 | 3520 | 3980 | 3620 | 3970 | 3000 |  | 69140
Steam Mass Flow | 0 | 0 | 0 | 121.094 | 0 | 137.246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4019.299 | 52.06 | 81.172 | 0 | 0 | 0 | 0 | 0 | 5727.874 | 6.935 | 3.029 | 0 | 0 | 0 | 0 | 0 | 8.119 | 0 |  | 10156.828
Water (m3)
Area | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | MTD | Target | Diff | %
Total water consumption | 7.1023 | 7.5081 | 11.7097 |  |  | 13.5017 | 12.2346 | 10.7001 | 19.9282 | 15.2744 |  |  | 35.8771 | 7.3419 | 12.8403 | 12.7099 | 8.2971 |  |  |  | 5.516 | 6.2637 | 4.2282 | 10.215 |  | 72.7273 | 6.7756 | 7.2216 | 8.5085 | 5.5969 | 16.3355 |  | 9.5522 | 10.2 | 0.64779 | 93.6491
[33 empty] | 0 |  |  | #DIV/0!
CO2 (kg./Hl.) KPI | 4.8692 | 3.6925 | 5.4149 |  |  | 6.6147 | 4.6671 | 5.3868 | 5.8973 | 9.9489 |  |  | 12.3183 | 3.8069 | 9.1505 | 7.1672 | 9.9794 |  |  |  | 4.7827 | 3.9528 | 3.2076 | 5.5412 |  | 0 | 3.8518 | 5.5685 | 4.3858 | 3.9624 | 6.8232 |  | 5.2293 | 5 | -0.22925 | 104.5851
CO2 Filler (kg./Hl.) KPI | 0.83636 | 0.80222 | 0.97096 |  |  | 0.86127 | 0.80918 | 0.76318 | 0.87005 | 0.93946 |  |  | 1.2426 | 1.0026 | 0.99909 | 0.8728 | 0.91029 |  |  |  | 0.77977 | 0.75701 | 0.67039 | 0.81776 |  | 0.083196 | 0.78762 | 0.80167 | 0.64403 | 1.3314 | 1.25 |  | 0.86218 | 1.7 | 0.83782 | 50.7163
Electricity (Kwh./Hl.) KPI | 16.6139 | 15.2023 | 32.0392 |  |  | 36.2562 | 30.4364 | 22.409 | 40.7793 | 41.5335 |  |  | 111.7732 | 21.2127 | 26.51 | 20.9187 | 22.8214 |  |  |  | 30.0639 | 12.9349 | 13.5856 | 24.1282 |  | 295.0964 | 16.3071 | 16.6132 | 15.4434 | 16.2278 | 32.4303 |  | 26.2699 | 22 | -4.2699 | 119.4086
[33 empty] | 0 |  |  | #DIV/0!
Fuel (L/Hl.) KPI | 5.9941 | 5.631 | 10.4575 |  |  | 14.8636 | 9.3676 | 8.1536 | 11.5614 | 6.2619 |  |  | 37.5708 | 6.4718 | 8.206 | 6.3549 | 6.5008 |  |  |  | 12.5944 | 4.6674 | 5.0447 | 7.1313 |  | 41.8733 | 6.1629 | 6.9258 | 6.3507 | 6.5545 | 12.0409 |  | 7.6175 | 7.2 | -0.41753 | 105.799
Total Bottles Washed | [32 empty] | 0 |  | .
Bottle Washer (Including rejects) | [32 empty] | #DIV/0! | 2.6 | #DIV/0!
CO2 to Liqufier (kg.) | 49.09 | 84.01 | 43.98 | 0 | 0 | 60.42 | 41.02 | 22.3 | 0 | 0 | 0 | 0 | 42.6 | 22.84 | 0 | 15.03 | 50.3 | 0 | 0 | 0 | 36.01 | 95.25 | 87.87 | 173.18 | 0 | 0 | 257.62 | 463.9 | #REF! | #REF! | 109.93 |  | #REF!
CO2 recovered (Kg - liquid) | [32 empty] | 0
CO2 liquid conversion efficiency | Wed: 0%; Thu: 0%; Fri: 0%; Tue: 0%; Wed: 0%; Mon: 0%; Tue: 0%; Thu: 0%; Fri: 0%; Tue: 0%; Wed: 0%; Thu: 0%; Fri: 0%; Mon: 0%; Tue: 0%; Wed: #REF!; Thu: #REF!; Fri: 0% |  | #REF!
Water Recovered (m3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | 0 |  | #REF!
Tanks on Collection
Into RO | Wed: _; Thu: 250; Mon: _; Tue: _; Fri: _ |  | 250
| 9895 |  | 9467 | 5362 | 3638 | 9318 | 9130 | 9152 | 8042 | 7097 | 5296 | 4670 | 7259 | 7801 | 8981 | 8756 | 8004 | 5271 | 4653 | 3787 | 9429 | 8508 | 9318 | 10015 | 4778 | 5356 | 9314 | 9547 | 8803 | 9829 | 8080 |  | 238437
9881
Note on A69: RAntoine: Line deleted by MD on April 20, 2011. Do not reinsert
Note on B74: Delano Pasea: Tank A 1200 kgs Tank B 0 kgs Tank C 24900 Kgs Mobile approx. 0 kgs
Note on C74: Delano Pasea: Tank A 0 kgs Tank B 0 kgs Tank C 23200 Kgs Mobile approx. 0 kgs
Note on D74: Delano Pasea: Tank A 0 kgs Tank B 0 kgs Tank C 20800 Kgs Mobile approx. 0 kgs
Note on E74: Delano Pasea: Tank A 0 kgs Tank B 0 kgs Tank C19200 Kgs Mobile approx. 17000 kgs
Note on F74: Delano Pasea: Tank A 0 kgs Tank B 0 kgs Tank C19200 Kgs Mobile approx. 17000 kgs
Note on G74: Delano Pasea: Tank A 0 kgs Tank B 0 kgs Tank C19200 Kgs Mobile approx. 17000 kgs
Note on H74: Delano Pasea: Tank A 0 kgs Tank B 0 kgs Tank C17500 Kgs Mobile approx. 17000 kgs
Note on I74: Delano Pasea: Tank A 0 kgs Tank B 0 kgs Tank C17500 Kgs Mobile approx. 15600 kgs
Note on J74: Delano Pasea: Tank A 6600 kgs Tank B 0 kgs Tank C 25700 Kgs Mobile approx. 0 kgs
Note on K74: Delano Pasea: Tank A 5300 kgs Tank B 0 kgs Tank C 25700 Kgs Mobile approx. 0 kgs
Note on L74: Delano Pasea: Tank A 3600 kgs Tank B 0 kgs Tank C 25700 Kgs Mobile approx. 0 kgs
Note on M74: Delano Pasea: Tank A 3600 kgs Tank B 0 kgs Tank C 25700 Kgs Mobile approx. 0 kgs
Note on N74: Delano Pasea: Tank A 3600 kgs Tank B 0 kgs Tank C 25700 Kgs Mobile approx. 0 kgs
Note on O74: Delano Pasea: Tank A 2800 kgs Tank B 0 kgs Tank C 25700 Kgs Mobile approx. 0 kgs
Note on P74: Delano Pasea: Tank A 1400 kgs Tank B 0 kgs Tank C 25700 Kgs Mobile approx. 0 kgs
Note on Q74: Delano Pasea: Tank A 0 kgs Tank B 0 kgs Tank C 24000 Kgs Mobile approx. 0 kgs
Note on R74: Delano Pasea: Tank A 0 kgs Tank B 0 kgs Tank C 21000 Kgs Mobile approx. 0 kgs
Note on S74: Delano Pasea: Tank A 0 kgs Tank B 0 kgs Tank C 17500 Kgs Mobile approx. 16600 Kgs
Note on V74: Delano Pasea: Tank A 0 kgs Tank B 0 kgs Tank C 17500 Kgs Mobile approx. 16600 kgs
Note on W74: Delano Pasea: Tank A 0 kgs Tank B 0 kgs Tank C 17500 Kgs Mobile approx. 15100 kgs
Note on X74: Delano Pasea: Tank A 5800 kgs Tank B 0 kgs Tank C 25700 Kgs Mobile approx. 00 kgs
Note on Y74: Delano Pasea: Tank A 3600 kgs Tank B 0 kgs Tank C 25700 Kgs Mobile approx. 00 kgs
Note on Z74: Delano Pasea: Tank A 1300 kgs Tank B 0 kgs Tank C 25700 Kgs Mobile approx. 00 kgs
Note on AA74: Delano Pasea: Tank A 1300 kgs Tank B 0 kgs Tank C 25700 Kgs Mobile approx. 00 kgs
Note on AB74: Delano Pasea: Tank A 1300 kgs Tank B 0 kgs Tank C 25700 Kgs Mobile approx. 00 kgs
Note on AC74: Delano Pasea: Tank A 0 kgs Tank B 0 kgs Tank C 24800 Kgs Mobile approx. 00 kgs
Note on AD74: Delano Pasea: Tank A 0 kgs Tank B 0 kgs Tank C 21600 Kgs Mobile approx. 00 kgs
Note on AE74: Delano Pasea: Tank A 0 kgs Tank B 0 kgs Tank C 19100 Kgs Mobile approx. 00 kgs
Note on AF74: Delano Pasea: Tank A 0 kgs Tank B 0 kgs Tank C 16700 Kgs Mobile approx. 00 kgs
Note on AG74: Delano Pasea: Tank A 0 kgs Tank B 0 kgs Tank C 15000 Kgs Mobile approx. 00 kgs

## Water Analysis. '25
DAILY WATER CONSUMPTION FOR OCTOBER 2025
| Nawasa | Nawasa Daily | Service Water | RO - Well | RO - Nawasa | RO - Nawasa | Permeate #1 | Permeate #1 | Permeate #2 | Permeate #2 | Total Permeate | Brewhouse | Bottle Filler | Plant Cons
DATE | Supply (m3) | Consump. (m3) | Consump (m3) | Intake (m3) | Intake (m3) | Consump. (m3) | (m3) | Produced (m3) | (m3) | Produced (m3) | Produced (m3) | (m3) | (m3) | Tot.(Hl) | Comments | Total Prod. | Water
31 | [16 empty] | Hl/Hl
1 | 197585 | 232 | 32 | 43045 | 1316136 | 200 | 97122 | 0 | 1316136 | -1316136 | -1316136 | 0 | 32 | 464 |  |  | #DIV/0!
2 | 197817 | 251 | 1 | 0 | 1316336 | 250 | 97122 | 0 | 0 | 0 | 0 | 0 | 0 | 502 |  |  | #DIV/0!
3 | 198068 | 148 | -60 | 0 | 1316586 | 208 | 97122 | 0 | 0 | 0 | 0 | 0 | 49 | 296 |  |  | #DIV/0!
4 | 198216 | 10 | -16 | 0 | 1316794 | 26 | 97122 | 0 | 0 | 0 | 0 | 0 | 3 | 20 |  |  | #DIV/0!
5 | 198226 | 27 | -75 | 0 | 1316820 | 102 | 97122 | 0 | 0 | 0 | 0 | 0 | 0 | 54 |  |  | #DIV/0!
6 | 198253 | 219 | 85 | 0 | 1316922 | 134 | 97122 | 0 | 0 | 21430 | 21430 | 0 | 16 | 438 |  |  | #DIV/0!
7 | 198472 | 116 | -148 | 0 | 1317056 | 264 | 97122 | 0 | 21430 | -21430 | -21430 | 0 | 17 | 232 |  |  | #DIV/0!
8 | 198588 | 234 | 20 | 0 | 1317320 | 214 | 97122 | 0 | 0 | 0 | 0 | 0 | 19 | 468 |  |  | #DIV/0!
9 | 198822 | 207 | 13 | 0 | 1317534 | 194 | 97122 | 0 | 0 | 0 | 0 | 0 | 10 | 414 |  |  | #DIV/0!
10 | 199029 | 136 | 5 | 0 | 1317728 | 131 | 97122 | 0 | 0 | 0 | 0 | 0 | 10 | 272 |  |  | #DIV/0!
11 | 199165 | 0 | -116 | 0 | 1317859 | 116 | 97122 | 0 | 0 | 0 | 0 | 0 | 2 | 0 |  |  | #DIV/0!
12 | 199165 | 0 | 0 | 0 | 1317975 | 0 | 97122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | #DIV/0!
13 | 199165 | 53 | -235 | 0 | 1317975 | 288 | 97122 | 0 | 0 | 0 | 0 | 0 | 7 | 106 |  |  | #DIV/0!
14 | 199218 | 141 | 104 | 0 | 1318263 | 37 | 97122 | 0 | 0 | 0 | 0 | 0 | 22 | 282 |  |  | #DIV/0!
15 | 199359 | 338 | 237 | 0 | 1318300 | 101 | 97122 | 0 | 0 | 0 | 0 | 0 | 25 | 676 |  |  | #DIV/0!
16 | 199697 | 348 | 155 | 0 | 1318401 | 193 | 97122 | 0 | 0 | 0 | 0 | 0 | 30 | 696 |  |  | #DIV/0!
17 | 200045 | 152 | 5 | 0 | 1318594 | 147 | 97122 | 0 | 0 | 0 | 0 | 0 | 21 | 304 |  |  | #DIV/0!
18 | 200197 | 70 | 25 | 0 | 1318741 | 45 | 97122 | 0 | 0 | 0 | 0 | 0 | 1 | 140 |  |  | #DIV/0!
19 | 200267 | 0 | 0 | 0 | 1318786 | 0 | 97122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | #DIV/0!
20 | 200267 | 0 | -200 | 0 | 1318786 | 200 | 97122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | #DIV/0!
21 | 200267 | 0 | 0 | 0 | 1318986 | 0 | 97122 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  |  | #DIV/0!
22 | 200267 | 245 | 90 | 0 | 1318986 | 155 | 97122 | 0 | 0 | 0 | 0 | 0 | 30 | 490 |  |  | #DIV/0!
23 | 200512 | 67 | -170 | 0 | 1319141 | 237 | 97122 | 0 | 0 | 0 | 0 | 0 | 31 | 134 |  |  | #DIV/0!
24 | 200579 | 127 | -184 | 0 | 1319378 | 311 | 97122 | 0 | 0 | 0 | 0 | 0 | 26 | 254 |  |  | #DIV/0!
25 | 200706 | 0 | 0 | 0 | 1319689 | 0 | 97122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | #DIV/0!
26 | 200706 | 132 | 132 | 0 | 1319689 | 0 | 97122 | 0 | 0 | 0 | 0 | 0 | 0 | 264 |  |  | #DIV/0!
27 | 200838 | 277 | 161 | 0 | 1319689 | 116 | 97122 | 0 | 0 | 0 | 0 | 0 | 32 | 554 |  |  | #DIV/0!
28 | 201115 | 284 | 146 | 0 | 1319805 | 138 | 97122 | 0 | 0 | 0 | 0 | 0 | 31 | 568 |  |  | #DIV/0!
| 201399 |  | 0 |  | 1319943 |  | 97122
Total |  | 3814 | 7 |  |  | 3807 |  | 0 | 1337566 | -1316136 | -1316136 | 0 | 431 | 7628 | 0 | 0 | #DIV/0!