## Entries March 2026
| ENTRIES FOR DAILY CONS. MONITOR | [12 empty] | ENTRIES FOR DAILY CONS. MONITOR
Service 227.3 cubic meters (2273 Hls)Filtered 189.3 cubic meters(1893 Hls)
|  |  | FUEL | [5 empty] | ELECT. |  | CO2 |  |  | WATER | [17 empty] | CO2 Scrubber (m3) | Supply to Washdown Area (m3) | Supply to RUs (m3) | Steam Mass Flow Meter | CO2 TANKS' READING
| Boilers tot. | Boiler 1 | Gen. meter | Tank level | Boiler 1 | Boiler 2 | Gen | Meter1 | Meter 2 | Gen Meter | Consumption (FILTRATION) (kg) | Consumption (Totalizer Flowmeter) | Consumption (Filler) (kg) | Nawasa Meter (m3) | Annandale Supply (m3) | Service Supply to Plant (m3) | Cellars/Filtration (m3) | Brewhouse Meter (m3) | Cellars/Process Areas (m3) | Pasteuriser (m3) | Water Plant-Nawasa Annadale (m3) | Water Plant-Well # 1 (m3) | CIP Process | Bottle Washer | Boiler | Permeate #1 | Permeate #2 | Bottle Filler (m3) | RO # 1 Totaliser (m3) | RO # 2 Totaliser (m3) | Recovered Water (m3) |  |  |  |  | Tank "C" | Tank "A" | Tank "B" | Mobile Tanker
DATE | (liters) | (liters) | (Imp. gals) | (inches) | Hrs | Hrs | Hrs. | (Kwhr) | (Kwhr) | (Kwhr) |  | (kg) | [10 empty] | (m3) | (m3) | (m3) | [10 empty] | inH2O | (Kg.) | (Kg.) | (pounds)
1 | 8038470 |  |  | 64 | 8155.3 | 68225 |  | 658766 |  | 468000 | 15090.84 | 330096.03 | 51927.31 | 222322 | 57590 | 953598 |  | 75054 |  | 22400 | 1336777 |  | 42669 | 56470 | 12310 | 97122 |  | 3717 | 262484 | [5 empty] | 7357397.737
2 | 8040450 |  |  | 64 | 8171.4 | 68225 |  | 663332 |  | 468000 | 15090.84 | 330096.03 | 51927.31 | 222505 | 57590 | 953678 |  | 75123 |  | 22401 | 1336777 |  | 42673 | 56499 | 12323 | 97122 |  | 3717 | 262484 | [5 empty] | 7357397.737
3 | 8044200 |  |  | 64 | 8191.6 | 68225 |  | 670768 |  | 468000 | 15203.41 | 332304.56 | 52384.23 | 222790 | 57726 | 954045 |  | 75250 |  | 22443 | 1336915 |  | 42713 | 56700 | 12364 | 97122 |  | 3753 | 262484 | [5 empty] | 7357397.737
4 | 8047470 |  |  | 64 | 8212.3 | 68225 |  | 677104 |  | 468000 | 15280.54 | 335277.31 | 52744.9 | 222917 | 57937 | 954377 |  | 75381 |  | 22456 | 1337142 |  | 42749 | 56844 | 12394 | 97122 |  | 3782 | 262484 | [5 empty] | 7357397.737
5 | 8051260 |  |  | 64 | 8233.7 | 68225 |  | 684285 |  | 468000 | 15356.77 | 337290.41 | 53133.84 | 223264 | 58102 | 954723 |  | 75519 |  | 22472 | 1337316 |  | 42815 | 57001 | 12429 | 97122 |  | 3812 | 262484 | [5 empty] | 7357397.737
6 | 8054670 |  |  | 64 | 8254.1 | 68225 |  | 690727 |  | 468000 | 15426.56 | 338762.72 | 53377.11 | 223447 | 58380 | 954974 |  | 75695 |  | 22480 | 1337607 |  | 42861 | 57108 | 12459 | 97122 |  | 3836 | 262484 | [5 empty] | 7357397.737
7 | 8057590 |  |  | 64 | 8271.8 | 68225 |  | 696840 |  | 468000 | 15584 | 340551.25 | 53633.38 | 223536 | 58623 | 955230 |  | 75810 |  | 22492 | 1337863 |  | 42911 | 57213 | 12486 | 97122 |  | 3860 | 262484 | [5 empty] | 7357397.737
8 | 8058020 |  |  | 64 | 8274.9 | 68225 |  | 700555 |  | 468000 | 15584.61 | 340551.25 | 53633.38 | 223537 | 58693 | 955330 |  | 75810 |  | 22492 | 1337938 |  | 42911 | 57257 | 12490 | 97122 |  | 3860 | 262484 | [5 empty] | 7357539.931
9 | 8060400 |  |  | 64 | 8290.3 | 68225 |  | 705151 |  | 468000 | 15663.48 | 341815.94 | 53809.97 | 223657 | 58815 | 955523 |  | 75810 |  | 22500 | 1338066 |  | 42916 | 57372 | 12519 | 97122 |  | 3877 | 262484 | [5 empty] | 7357539.931
10 | 8063780 |  |  | 64 | 8311.8 | 68225 |  | 712499 |  | 468000 | 15806.31 | 343926 | 54095.85 | 223863 | 59025 | 955795 |  | 75958 |  | 22510 | 1338287 |  | 42972 | 57520 | 12555 | 97122 |  | 3905 | 262484 | [5 empty] | 7357539.931
11 | 8067520 |  |  | 64 | 8332.7 | 68225 |  | 718524 |  | 468000 | 15851.58 | 346928.47 | 54362.86 | 224183 | 59125 | 956117 |  | 76118 |  | 22517 | 1338392 |  | 42996 | 57668 | 12583 | 97122 |  | 3930 | 262538 | [5 empty] | 7357539.931
12 | 8071000 |  |  | 64 | 8353.5 | 68225 |  | 725188 |  | 468000 | 15930.02 | 349805.47 | 54649.21 | 224585 | 59288 | 956440 |  | 76319 |  | 22525 | 1338563 |  | 43057 | 57823 | 12613 | 97122 |  | 3958 | 262581 | [5 empty] | 7357539.931
13 | 8074760 |  |  | 64 | 8374.6 | 68225 |  | 732948 |  | 468000 | 16240.73 | 353151.91 | 55022.17 | 224838 | 59518 | 956773 |  | 76465 |  | 22528 | 1338805 |  | 43111 | 58005 | 12647 | 97122 |  | 3988 | 262611 | [5 empty] | 7357539.931
14 | 8078000 |  |  | 64 | 8394.1 | 68225 |  | 738978 |  | 468000 | 16331.48 | 355509.63 | 55258.43 | 225014 | 59733 | 957014 |  | 76639 |  | 22535 | 1339029 |  | 43144 | 58112 | 12672 | 97122 |  | 4010 | 262611 | [5 empty] | 7357539.931
15 | 8079730 |  |  | 64 | 8408.5 | 68225 |  | 743065 |  | 468000 | 16331.48 | 355561.5 | 55258.43 | 225014 | 59943 | 957089 |  | 76788 |  | 22535 | 1339250 |  | 43174 | 58114 | 12682 | 97122 |  | 4013 | 262611 | [5 empty] | 7357539.931
16 | 8081280 |  |  | 64 | 8419.2 | 68225 |  | 746384 |  | 468000 | 16353.54 | 355587.11 | 55258.43 | 225061 | 59990 | 957165 |  | 76842 |  | 22535 | 1339301 |  | 43179 | 58164 | 12694 | 97122 |  | 4013 | 262611 | [5 empty] | 7357655.219
17 | 8083390 |  |  | 64 | 8433.7 | 68225 |  | 750334 |  | 468000 | 16412.52 | 356512.94 | 55356.5 | 225207 | 60114 | 957314 |  | 76905 |  | 22540 | 1339430 |  | 43204 | 58218 | 12717 | 97122 |  | 4021 | 262611 | [5 empty] | 7357655.219
18 | 8084100 |  |  | 64 | 8438.4 | 68225 |  | 753027 |  | 468000 | 16412.52 | 356645.75 | 55356.5 | 225215 | 60152 | 957544 |  | 76905 |  | 22540 | 1339470 |  | 43204 | 58219 | 12733 | 97122 |  | 4021 | 262611 | [5 empty] | 7357655.219
19 | 8086830 |  |  | 64 | 8456.4 | 68225 |  | 758864 |  | 468000 | 16705.26 | 358333.71 | 55643.12 | 225385 | 60256 | 957599 |  | 76945 |  | 22544 | 1339580 |  | 43267 | 58378 | 12777 | 97122 |  | 4048 | 262611 | [5 empty] | 7357655.219
20 | 8090980 |  |  | 64 | 8477.7 | 68225 |  | 764386 |  | 468000 | 17198.44 | 361837.41 | 56052.65 | 225748 | 60418 | 957963 |  | 77084 |  | 22552 | 1339750 |  | 43304 | 58537 | 12814 | 97122 |  | 4079 | 262611 | [5 empty] | 7357655.219
21 | 8094460 |  |  | 64 | 8498.2 | 68225 |  | 770513 |  | 468000 | 17646.19 | 364245.25 | 56328.42 | 226068 | 60646 | 958257 |  | 77225 |  | 22554 | 1339989 |  | 43353 | 58686 | 12857 | 97122 |  | 4108 | 262611 | [5 empty] | 7357655.219
22 | 8096130 |  |  | 64 | 8511.3 | 68225 |  | 774223 |  | 468000 | 17818.83 | 364683.53 | 56328.42 | 226214 | 60761 | 958381 |  | 77358 |  | 22554 | 1340110 |  | 43369 | 58715 | 12874 | 97122 |  | 4109 | 262611 | [5 empty] | 7357767.354
23 | 8098250 |  |  | 64 | 8526.7 | 68225 |  | 777898 |  | 468000 | 17818.83 | 364683.53 | 56328.42 | 226294 | 60887 | 958400 |  | 77552 |  | 22554 | 1340243 |  | 43369 | 58715 | 12894 | 97122 |  | 4109 | 262611 | [5 empty] | 7357777.366
24 | 8102140 |  |  | 64 | 8549.6 | 68225 |  | 785064 |  | 468000 | 18132.17 | 367264.11 | 56703.61 | 226379 | 61129 | 958619 |  | 77689 |  | 22556 | 1340494 |  | 43392 | 58823 | 12925 | 97122 |  | 4146 | 262649 | [5 empty] | 7358466.1
25 | 8105350 |  |  | 64 | 8569.1 | 68225 |  | 790708 |  | 468000 | 18688.64 | 369347.91 | 56926.22 | 226497 | 61229 | 958833 |  | 77819 |  | 22556 | 1340675 |  | 43433 | 58889 | 12954 | 97122 |  | 4174 | 262658 | [5 empty] | 7359251.491
26 | 8107800 |  |  | 64 | 8585.9 | 68225 |  | 797041 |  | 468000 | 18768.53 | 370939.06 | 57127.51 | 226716 | 61505 | 959020 |  | 77931 |  | 22556 | 1340891 |  | 43496 | 58953 | 12971 | 97122 |  | 4187 | 262716 | [5 empty] | 7359251.491
27 | 8110040 |  |  | 64 | 8602.2 | 68225 |  | 803395 |  | 468000 | 18768.53 | 372198.03 | 57331.39 | 226950 | 61606 | 959197 |  | 78048 |  | 22556 | 1340996 |  | 43524 | 59047 | 12979 | 97122 |  | 4192 | 262804 | [5 empty] | 7359251.491
28 | 8112240 |  |  | 64 | 8617 | 68225 |  | 808058 |  | 468000 | 18824.68 | 373697.03 | 57560.69 | 227090 | 61675 | 959360 |  | 78074 |  | 22556 | 1341069 |  | 43533 | 59132 | 12993 | 97122 |  | 4214 | 262820 | [5 empty] | 7359876.367
29 | 8112240 |  |  | 64 | 8617 | 68225 |  | 810916 |  | 468000 | 18824.68 | 373697.03 | 57560.69 | 227100 | 61722 | 959383 |  | 78079 |  | 22556 | 1341117 |  | 43533 | 59136 | 12993 | 97122 |  | 4214 | 262820 | [5 empty] | 7359876.367
30 | 8112240 |  |  | 64 | 8617 | 68225 |  | 813701 |  | 468000 | 18824.68 | 373697.03 | 57560.69 | 227100 | 61722 | 959383 |  | 78079 |  | 22556 | 1341117 |  | 43533 | 59136 | 12993 | 97122 |  | 4214 | 262820 | [5 empty] | 7359876.367
31 | 8115940 |  |  | 64 | 8639 | 68225 |  | 818889 |  | 468000 | 18910.55 | 375802.41 | 57836.48 | 227291 | 61911 | 959700 |  | 78133 |  | 22557 | 1341315 |  | 43601 | 59282 | 13023 | 97122 |  | 4238 | 262820 | [5 empty] | 7360485.676
1 | 8119100 |  |  | 64 | 8658.6 | 68225 |  | 825474 |  | 468000 | 19274.65 | 377633.25 | 58084.65 | 227533 | 61994 | 959930 |  | 78247 |  | 22559 | 1341402 |  | 43639 | 59389 | 13039 | 97122 |  | 4267 | 262820 | [5 empty] | 7360518.265

## Utility Analysis March 2026
GRENADA BREWERIES LIMITED
UTILITY ANALYSIS
MONTH: | [7 empty] | 2007-08-01
DATE |  |  | ELECTRICITY GRENLEC | Solar System CARIB | % (Solar/Total Usage) | CARIB GENSET | ELECTRICITY TOTAL | WATER | FUEL | CO2 | PRODUCTION - HL |  |  |  |  | UTILITY RATIOS
| METER 1 | METER 2 | [13 empty] | Elect | Water | Fuel | CO2
[6 empty] | USAGE (kwh) | USAGE (kwh) | USAGE (Hl) | USAGE (l) | USAGE (Kg.) | BREWED | BOTTLED | KEGS | OTHER | TOTAL | KWH/Hl | Hl/hl | Litres/hl | kg./Hl
1 | 4566 | 0 | 4566 | 1593.9 | 25.88% | 0 | 6159.9 | 1830 | 1980 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 7436 | 0 | 7436 | 1245.6 | 14.35% | 0 | 8681.6 | 4210 | 3750 | 1900 | 0 | 0 | 0 | 0 | 434.742 | 19.9695 | 9.6839 | 8.6258 | 4.3704
3 | 6336 | 0 | 6336 | 1477.5 | 18.91% | 0 | 7813.5 | 3380 | 3270 | 1700 | 0 | 0 | 0 | 0 | 405.042 | 19.2906 | 8.3448 | 8.0732 | 4.1971
4 | 7181 | 0 | 7181 | 1608.8 | 18.3% | 0 | 8789.8 | 5120 | 3790 | 2700 | 0 | 0 | 0 | 0 | 419.364 | 20.9598 | 12.209 | 9.0375 | 6.4383
5 | 6442 | 0 | 6442 | 1329.1 | 17.1% | 0 | 7771.1 | 4610 | 3410 | 1400 | 0 | 0 | 0 | 0 | 278.838 | 27.8696 | 16.5329 | 12.2293 | 5.0208
6 | 6113 | 0 | 6113 | 1332.2 | 17.89% | 0 | 7445.2 | 3320 | 2920 | 1900 | 0 | 0 | 0 | 0 | 305.8452 | 24.343 | 10.8552 | 9.5473 | 6.2123
7 | 3715 | 0 | 3715 | 1469.7 | 28.35% | 0 | 5184.7 | 710 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 4596 | 0 | 4596 | 1555.3 | 25.28% | 0 | 6151.3 | 2420 | 2380 | 2200 | 0 | 0 | 0 | 0 | 239.58 | 25.6753 | 10.101 | 9.9341 | 9.1827
9 | 7348 | 0 | 7348 | 1688.7 | 18.69% | 0 | 9036.7 | 4160 | 3380 | 2400 | 0 | 0 | 0 | 0 | 357.918 | 25.248 | 11.6228 | 9.4435 | 6.7054
10 | 6025 | 0 | 6025 | 1618 | 21.17% | 0 | 7643 | 4200 | 3740 | 1700 | 0 | 0 | 0 | 0 | 459.096 | 16.6479 | 9.1484 | 8.1464 | 3.7029
11 | 6664 | 0 | 6664 | 1457 | 17.94% | 0 | 8121 | 5650 | 3480 | 3200 | 0 | 0 | 0 | 0 | 416.79 | 19.4846 | 13.556 | 8.3495 | 7.6777
12 | 7760 | 0 | 7760 | 1050.1 | 11.92% | 0 | 8810.1 | 4830 | 3760 | 2500 | 0 | 0 | 0 | 0 | 515.328 | 17.0961 | 9.3727 | 7.2963 | 4.8513
13 | 6030 | 0 | 6030 | 1686.1 | 21.85% | 0 | 7716.1 | 3910 | 3240 | 2500 | 0 | 0 | 0 | 0 | 309.804 | 24.9064 | 12.6209 | 10.4582 | 8.0696
14 | 4087 | 0 | 4087 | 1658 | 28.86% | 0 | 5745 | 2100 | 1730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 3319 | 0 | 3319 | 1365.1 | 29.14% | 0 | 4684.1 | 940 | 1550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 3950 | 0 | 3950 | 1666.2 | 29.67% | 0 | 5616.2 | 2700 | 2110 | 800 | 0 | 0 | 0 | 0 | 114.51 | 49.0455 | 23.5787 | 18.4263 | 6.9863
17 | 2693 | 0 | 2693 | 1560.7 | 36.69% | 0 | 4253.7 | 460 | 710 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 5837 | 0 | 5837 | 1523.6 | 20.7% | 0 | 7360.6 | 2740 | 2730 | 1500 | 0 | 0 | 0 | 0 | 364.584 | 20.189 | 7.5154 | 7.488 | 4.1143
19 | 5522 | 0 | 5522 | 1625.4 | 22.74% | 0 | 7147.4 | 5250 | 4150 | 2300 | 0 | 0 | 0 | 0 | 726.528 | 9.8377 | 7.2261 | 5.7121 | 3.1657
20 | 6127 | 0 | 6127 | 1583.2 | 20.53% | 0 | 7710.2 | 5480 | 3480 | 2500 | 0 | 0 | 0 | 0 | 487.74 | 15.808 | 11.2355 | 7.1349 | 5.1257
21 | 3710 | 0 | 3710 | 1717.9 | 31.65% | 0 | 5427.9 | 2610 | 1670 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 3675 | 0 | 3675 | 1770.6 | 32.51% | 0 | 5445.6 | 2060 | 2120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 7166 | 0 | 7166 | 1425.4 | 16.59% | 0 | 8591.4 | 3270 | 3890 | 2000 | 0 | 0 | 0 | 0 | 613.074 | 14.0136 | 5.3338 | 6.3451 | 3.2622
24 | 5644 | 0 | 5644 | 1590.1 | 21.98% | 0 | 7234.1 | 2180 | 3210 | 2243.1818 | 0 | 0 | 0 | 0 | 392.238 | 18.4431 | 5.5579 | 8.1838 | 5.7189
25 | 6333 | 0 | 6333 | 1399.2 | 18.1% | 0 | 7732.2 | 4950 | 2450 | 1326.3636 | 0 | 0 | 0 | 0 | 325.776 | 23.7347 | 15.1945 | 7.5205 | 4.0714
26 | 6354 | 0 | 6354 | 1440.4 | 18.48% | 0 | 7794.4 | 3350 | 2240 | 2795.4545 | 0 | 0 | 0 | 0 | 337.788 | 23.0748 | 9.9175 | 6.6314 | 8.2758
27 | 4663 | 0 | 4663 | 1553.4 | 24.99% | 0 | 6216.4 | 2090 | 2200 | 1100 | 0 | 0 | 0 | 0 | 397.782 | 15.6277 | 5.2541 | 5.5307 | 2.7653
28 | 2858 | 0 | 2858 | 1446.6 | 33.61% | 0 | 4304.6 | 570 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 2785 | 0 | 2785 | 1541.6 | 35.63% | 0 | 4326.6 | 0 | 0 | 3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 5188 | 0 | 5188 | 1369.8 | 20.89% | 0 | 6557.8 | 3800 | 3700 | 1100 | 0 | 0 | 0 | 0 | 447.81 | 14.6442 | 8.4857 | 8.2624 | 2.4564
31 | 6585 | 0 | 6585 | 1201.7 | 15.43% | 0 | 7786.7 | 3250 | 3160 | 1200 |  |  |  |  | 436.392 | 17.8434 | 7.4474 | 7.2412 | 2.7498
MTD
|  |  | Kwhr |  |  | Kwhr | Kwhr | Hl | L | kg. | hl | hl | hl | hl | hl | Elect | Water | Fuel | CO2
Total |  |  | 166708 | 46550.9 | 21.83% | 0 | 213258.9 | 96150 | 80630 | 47666 | 0 | 0 | 0 | 0 | 8786.5692 | KWH/Hl | Hl/hl | Litres/hl | kg./Hl
|  |  | TOTAL | 213258.9 | [11 empty] | 24.271 | 10.9428 | 9.1765 | 5.4249
Note on E20: Alexander Dominguez-Ramon: Change of 13 PV Panels of 465 watts to 645 watss. (String 9 . Inverter #3)
Note on B25: Alexander Dominguez-Ramon: Glycol Pump OFF + RU System Off
Note on B26: Alexander Dominguez-Ramon: Glycol Pump OFF + RU System Off
Note on E26: Alexander Dominguez-Ramon: DataLogger #3 Failure WiFi connection. The energy generated on this day was estimated based on values from previous days.
Note on E27: Alexander Dominguez-Ramon: DataLogger #3 Failure WiFi connection. The energy generated on this day was estimated based on values from previous days.

## Steam Mass Flow
DATE | Steam Mass Flow Reading
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 142.194
8 | 0
9 | 0
10 | 0
11 | 0
12 | 0
13 | 0
14 | 0
15 | 115.288
16 | 0
17 | 0
18 | 0
19 | 0
20 | 0
21 | 112.135
22 | 10.012
23 | 688.734
24 | 785.391
25 | 0
26 | 0
27 | 624.876
28 | 0
29 | 0
30 | 609.309
31 | 32.589
3120.528

## Fuel
DAILY FUEL CONSUMPTION FOR MARCH 2026
DATE | Boiler 1 | Boiler 1 | Boiler 2 | Boiler 2 | Gen. | Gen | Boiler 1 sp. | Boiler 2 sp. | Gen. sp | Daily cons. | Total Prod.(HL) | Fuel(Litres/HL)
| Cons ( l ) | Hrs | Cons ( l ) | Hrs | Cons ( l ) | Hrs | cons (l/hr) | cons (l/hr) | Cons.(l/hr) | (litres)
1 | 1980 | 16.1 | 0 | 0 |  |  | 122.9814 | 0 | 0 | 1980 | 0 | 0
2 | 3750 | 20.2 | 0 | 0 |  |  | 185.6436 | 0 | 0 | 3750 | 434.742 | 8.6258
3 | 3270 | 20.7 | 0 | 0 |  |  | 157.971 | 0 | 0 | 3270 | 405.042 | 8.0732
4 | 3790 | 21.4 | 0 | 0 |  |  | 177.1028 | 0 | 0 | 3790 | 419.364 | 9.0375
5 | 3410 | 20.4 | 0 | 0 |  |  | 167.1569 | 0 | 0 | 3410 | 278.838 | 12.2293
6 | 2920 | 17.7 | 0 | 0 |  |  | 164.9718 | 0 | 0 | 2920 | 305.8452 | 9.5473
7 | 430 | 3.1 | 0 | 0 |  |  | 138.7097 | 0 | 0 | 430 | 0 | 0
8 | 2380 | 15.4 | 0 | 0 |  |  | 154.5455 | 0 | 0 | 2380 | 239.58 | 9.9341
9 | 3380 | 21.5 | 0 | 0 |  |  | 157.2093 | 0 | 0 | 3380 | 357.918 | 9.4435
10 | 3740 | 20.9 | 0 | 0 |  |  | 178.9474 | 0 | 0 | 3740 | 459.096 | 8.1464
11 | 3480 | 20.8 | 0 | 0 |  |  | 167.3077 | 0 | 0 | 3480 | 416.79 | 8.3495
12 | 3760 | 21.1 | 0 | 0 |  |  | 178.1991 | 0 | 0 | 3760 | 515.328 | 7.2963
13 | 3240 | 19.5 | 0 | 0 |  |  | 166.1538 | 0 | 0 | 3240 | 309.804 | 10.4582
14 | 1730 | 14.4 | 0 | 0 |  |  | 120.1389 | 0 | 0 | 1730 | 0 | 0
15 | 1550 | 10.7 | 0 | 0 |  |  | 144.8598 | 0 | 0 | 1550 | 0 | 0
16 | 2110 | 14.5 | 0 | 0 |  |  | 145.5172 | 0 | 0 | 2110 | 114.51 | 18.4263
17 | 710 | 4.7 | 0 | 0 |  |  | 151.0638 | 0 | 0 | 710 | 0 | 0
18 | 2730 | 18 | 0 | 0 |  |  | 151.6667 | 0 | 0 | 2730 | 364.584 | 7.488
19 | 4150 | 21.3 | 0 | 0 |  |  | 194.8357 | 0 | 0 | 4150 | 726.528 | 5.7121
20 | 3480 | 20.5 | 0 | 0 |  |  | 169.7561 | 0 | 0 | 3480 | 487.74 | 7.1349
21 | 1670 | 13.1 | 0 | 0 |  |  | 127.4809 | 0 | 0 | 1670 | 0 | 0
22 | 2120 | 15.4 | 0 | 0 |  |  | 137.6623 | 0 | 0 | 2120 | 0 | 0
23 | 3890 | 22.9 | 0 | 0 |  |  | 169.869 | 0 | 0 | 3890 | 613.074 | 6.3451
24 | 3210 | 19.5 | 0 | 0 |  |  | 164.6154 | 0 | 0 | 3210 | 392.238 | 8.1838
25 | 2450 | 16.8 | 0 | 0 |  |  | 145.8333 | 0 | 0 | 2450 | 325.776 | 7.5205
26 | 2240 | 16.3 | 0 | 0 |  |  | 137.4233 | 0 | 0 | 2240 | 337.788 | 6.6314
27 | 2200 | 14.8 | 0 | 0 |  |  | 148.6486 | 0 | 0 | 2200 | 397.782 | 5.5307
28 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
30 | 3700 | 22 |  | 0 |  |  | 168.1818 | 0 | 0 | 3700 | 447.81 | 8.2624
31 | 3160 | 19.6 |  | 0 |  |  | 161.2245 | 0 | 0 | 3160 | 436.392
MTD | 80630 | 503.3 | 0 | 0 |  |  | 160.2027 |  |  | 80630 | 8786.5692 | 9.1765 | 7.2 | 127.4515
AVE. | 2780.3448 | 17.3552 |  |  |  |  | cons (l/hr)

## Water
| DATE | Well Supply (m3) | Nawasa Supply (m3) | Annanale Supply (m3) | RO Water Plant Nawasa (m3) | Service Water Received (m3) | Service Water Supply to Plant (m3) | CO2 Scrubber (m3) | Brewhouse / Old Pepsi Area (m3) | Filtration/Cellars (m3) | Cellars/Process Area (m3) | Pasteuriser (m3) |  |  |  |  | Permeate Produced (m3) | Plant Cons. USAGE (Hl.) |  | Bottle Filler (m3) |  |  | Rus (m3) | Washdown Area (m3) | TOTAL SUPPLY (M3) | Total Prod.(HL) | Water KPI (Hl/Hl)
[13 empty] | CIP Process (m3) | Bottles Washer (m3) | Bottles Filler (m3) | Boiler Supply (m3) |  |  | ∑ Service Water to Processes |  | Water into RO #1 (m3) | Water into RO #2 (m3)
-
| 1 | 0 | 183 | 0 | 0 | 183 | 80 | 0 | 69 | 0 | 0 | 1 | 4 | 29 | 0 | 13 | 0 | 1830 | 34 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0
| 2 | 0 | 285 | 136 | 138 | 283 | 367 | 0 | 127 | 0 | 0 | 42 | 40 | 201 | 36 | 41 | 0 | 2830 | 283 | 36 | 0 | 0 | 0 | 0 | 421 | 434.742 | 9.6839
| 3 | 0 | 127 | 211 | 227 | 111 | 332 | 0 | 131 | 0 | 0 | 13 | 36 | 144 | 29 | 30 | 0 | 1110 | 193 | 29 | 0 | 0 | 0 | 0 | 338 | 405.042 | 8.3448
| 4 | 0 | 347 | 165 | 174 | 338 | 346 | 0 | 138 | 0 | 0 | 16 | 66 | 157 | 30 | 35 | 0 | 3380 | 239 | 30 | 0 | 0 | 0 | 0 | 512 | 419.364 | 12.209
| 5 | 0 | 183 | 278 | 291 | 170 | 251 | 0 | 176 | 0 | 0 | 8 | 46 | 107 | 24 | 30 | 0 | 1700 | 161 | 24 | 0 | 0 | 0 | 0 | 461 | 278.838 | 16.5329
| 6 | 0 | 89 | 243 | 256 | 76 | 256 | 0 | 115 | 0 | 0 | 12 | 50 | 105 | 24 | 27 | 0 | 760 | 167 | 24 | 0 | 0 | 0 | 0 | 332 | 305.8452 | 10.8552
| 7 | 0 | 1 | 70 | 75 | -4 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 4 | 0 | -40 | 44 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0
| 8 | 0 | 120 | 122 | 128 | 114 | 193 | 0 | 0 | 0 | 0 | 8 | 5 | 115 | 17 | 29 | 0 | 1140 | 128 | 17 | 0 | 0 | 0 | 0 | 242 | 239.58 | 10.101
| 9 | 0 | 206 | 210 | 221 | 195 | 272 | 0 | 148 | 0 | 0 | 10 | 56 | 148 | 28 | 36 | 0 | 1950 | 214 | 28 | 0 | 0 | 0 | 0 | 416 | 357.918 | 11.6228
| 10 | 0 | 320 | 100 | 105 | 315 | 322 | 0 | 160 | 0 | 0 | 7 | 24 | 148 | 25 | 28 | 0 | 3150 | 179 | 25 | 54 | 0 | 0 | 0 | 420 | 459.096 | 9.1484
| 11 | 0 | 402 | 163 | 171 | 394 | 323 | 0 | 201 | 0 | 0 | 8 | 61 | 155 | 28 | 30 | 0 | 3940 | 224 | 28 | 43 | 0 | 0 | 0 | 565 | 416.79 | 13.556
| 12 | 0 | 253 | 230 | 242 | 241 | 333 | 0 | 146 | 0 | 0 | 3 | 54 | 182 | 30 | 34 | 0 | 2410 | 239 | 30 | 30 | 0 | 0 | 0 | 483 | 515.328 | 9.3727
| 13 | 0 | 176 | 215 | 224 | 167 | 241 | 0 | 174 | 0 | 0 | 7 | 33 | 107 | 22 | 25 | 0 | 1670 | 147 | 22 | 0 | 0 | 0 | 0 | 391 | 309.804 | 12.6209
| 14 | 0 | 0 | 210 | 221 | -11 | 75 | 0 | 149 | 0 | 0 | 0 | 30 | 2 | 3 | 10 | 0 | -110 | 32 | 3 | 0 | 0 | 0 | 0 | 210 | 0 | 0
| 15 | 0 | 47 | 47 | 51 | 43 | 76 | 0 | 54 | 0 | 0 | 0 | 5 | 50 | 0 | 12 | 0 | 430 | 55 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0
| 16 | 0 | 146 | 124 | 129 | 141 | 149 | 0 | 63 | 0 | 0 | 5 | 25 | 54 | 8 | 23 | 0 | 1410 | 84 | 8 | 0 | 0 | 0 | 0 | 270 | 114.51 | 23.5787
| 17 | 0 | 8 | 38 | 40 | 6 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 16 | 0 | 60 | 1 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0
| 18 | 0 | 170 | 104 | 110 | 164 | 55 | 0 | 40 | 0 | 0 | 4 | 63 | 159 | 27 | 44 | 0 | 1640 | 226 | 27 | 0 | 0 | 0 | 0 | 274 | 364.584 | 7.5154
| 19 | 0 | 363 | 162 | 170 | 355 | 364 | 0 | 139 | 0 | 0 | 8 | 37 | 159 | 31 | 37 | 0 | 3550 | 204 | 31 | 0 | 0 | 0 | 0 | 525 | 726.528 | 7.2261
| 20 | 0 | 320 | 228 | 239 | 309 | 294 | 0 | 141 | 0 | 0 | 2 | 49 | 149 | 29 | 43 | 0 | 3090 | 200 | 29 | 0 | 0 | 0 | 0 | 548 | 487.74 | 11.2355
| 21 | 0 | 146 | 115 | 121 | 140 | 124 | 0 | 133 | 0 | 0 | 0 | 16 | 29 | 1 | 17 | 0 | 1400 | 45 | 1 | 0 | 0 | 0 | 0 | 261 | 0 | 0
| 22 | 0 | 80 | 126 | 133 | 73 | 19 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 730 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 0
| 23 | 0 | 85 | 242 | 251 | 76 | 219 | 0 | 137 | 0 | 0 | 2 | 23 | 108 | 37 | 31 | 0 | 760 | 133 | 37 | 38 | 0 | 0 | 0 | 327 | 613.074 | 5.3338
| 24 | 0 | 118 | 100 | 181 | 37 | 214 | 0 | 130 | 0 | 0 | 0 | 41 | 66 | 28 | 29 | 0 | 370 | 107 | 28 | 9 | 0 | 0 | 0 | 218 | 392.238 | 5.5579
| 25 | 0 | 219 | 276 | 216 | 279 | 187 | 0 | 112 | 0 | 0 | 0 | 63 | 64 | 13 | 17 | 0 | 2790 | 127 | 13 | 58 | 0 | 0 | 0 | 495 | 325.776 | 15.1945
| 26 | 0 | 234 | 101 | 105 | 230 | 177 | 0 | 117 | 0 | 0 | 0 | 28 | 94 | 5 | 8 | 0 | 2300 | 122 | 5 | 88 | 0 | 0 | 0 | 335 | 337.788 | 9.9175
| 27 | 0 | 140 | 69 | 73 | 136 | 163 | 0 | 26 | 0 | 0 | 0 | 9 | 85 | 22 | 14 | 0 | 1360 | 94 | 22 | 16 | 0 | 0 | 0 | 209 | 397.782 | 5.2541
| 28 | 0 | 10 | 47 | 48 | 9 | 23 | 0 | 5 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 90 | 4 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0
| 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 30 | 0 | 191 | 189 | 198 | 182 | 317 | 0 | 54 | 0 | 0 | 1 | 68 | 146 | 24 | 30 | 0 | 1820 | 215 | 24 | 0 | 0 | 0 | 0 | 380 | 447.81 | 8.4857
| 31 | 0 | 242 | 83 | 87 | 238 |  |  | 114 | 0 | 0 | 2 | 38 | 107 | 29 | 16 | 0 | 2380 |  | 29 | 0 | 0 | 0 | 0 | 325 | 436.392
MTD | total | 0 | 5211 | 4404 | 4625 | 4990 | 6102 |  | 3193 |  | 0 | 159 | 970 | 2919 | 550 | 729 | 0 | 49900 | 3901 | 550 | 336 |  |  |  | 9615 | 8786.5692 | 10.9428 | 10.2 | 107.2827
| Gals. |  | 1146420
| NAWASA Cost/gal |  | 0.01581
| Proxy NAWASA water Cost |  | 18124.9002
| Add basic charge |  | 278.97
18403.8702
| Proxy sewage charge (2/3) |  | 12269.2468
| Proxy MTD NAWASA cost |  | 30673.117
Note on S4: Note: this is not truly accurate since this includes the service water reading on the inlet and not the outlet side (meters to be installed there)

## Elec.March 2026
DAILY ELECTRICITY CONSUMPTION FOR MARCH 2026
DATE | Grenlec | In -house | Solar System | Total Cons. (KW-HR) | Total Prod.(HL) | KPI. Elect (KW-H/Hl)
| In-feed (Kwhr) | Gen. (Kwhr) | Gen. (Kwhr)
1 | 4566 | 0 | 1593.9 | 6159.9 | 0 | 0
2 | 7436 | 0 | 1245.6 | 8681.6 | 434.742 | 19.9695
3 | 6336 | 0 | 1477.5 | 7813.5 | 405.042 | 19.2906
4 | 7181 | 0 | 1608.8 | 8789.8 | 419.364 | 20.9598
5 | 6442 | 0 | 1329.1 | 7771.1 | 278.838 | 27.8696
6 | 6113 | 0 | 1332.2 | 7445.2 | 305.8452 | 24.343
7 | 3715 | 0 | 1469.7 | 5184.7 | 0 | 0
8 | 4596 | 0 | 1555.3 | 6151.3 | 239.58 | 25.6753
9 | 7348 | 0 | 1688.7 | 9036.7 | 357.918 | 25.248
10 | 6025 | 0 | 1618 | 7643 | 459.096 | 16.6479
11 | 6664 | 0 | 1457 | 8121 | 416.79 | 19.4846
12 | 7760 | 0 | 1050.1 | 8810.1 | 515.328 | 17.0961
13 | 6030 | 0 | 1686.1 | 7716.1 | 309.804 | 24.9064
14 | 4087 | 0 | 1658 | 5745 | 0 | 0
15 | 3319 | 0 | 1365.1 | 4684.1 | 0 | 0
16 | 3950 | 0 | 1666.2 | 5616.2 | 114.51 | 49.0455
17 | 2693 | 0 | 1560.7 | 4253.7 | 0 | 0
18 | 5837 | 0 | 1523.6 | 7360.6 | 364.584 | 20.189
19 | 5522 | 0 | 1625.4 | 7147.4 | 726.528 | 9.8377
20 | 6127 | 0 | 1583.2 | 7710.2 | 487.74 | 15.808
21 | 3710 | 0 | 1717.9 | 5427.9 | 0 | 0
22 | 3675 | 0 | 1770.6 | 5445.6 | 0 | 0
23 | 7166 |  | 1425.4 | 8591.4 | 613.074 | 14.0136
24 | 5644 | 0 | 1590.1 | 7234.1 | 392.238 | 18.4431
25 | 6333 | 0 | 1399.2 | 7732.2 | 325.776 | 23.7347
26 | 6354 | 0 | 1440.4 | 7794.4 | 337.788 | 23.0748
27 | 4663 | 0 | 1553.4 | 6216.4 | 397.782 | 15.6277
28 | 2858 | 0 | 1446.6 | 4304.6 | 0 | 0
29 | 2785 | 0 | 1541.6 | 2785 | 0 | 0
30 | 5188 | 0 | 1369.8 | 5188 | 447.81 | 11.5853
31 | 6585 |  | 1201.7 | 6585 |  |  |  | %
MTD | 166708 | 0 | 46550.9 | 209145.8 | 8350.1772 | 25.0469 | 22 | 113.8494
TARGET

## PROD.FIG.
PRODUCTION FOR MARCH 2026
DATE
| - | BOTTLED (Hl) | KEGS (Hl) | OTHER (Filtered) | Brewed | Transferred | TOTAL ( Hls)
Sunday | 1 | [5 empty] | 0
Monday | 2 | [5 empty] | 434.742
Tuesday | 3 | [5 empty] | 405.042
Wednesday | 4 | [5 empty] | 419.364
Thursday | 5 | [5 empty] | 278.838
Friday | 6 | [5 empty] | 305.8452
Saturday | 7 | [5 empty] | 0
Sunday | 8 | [5 empty] | 239.58
Monday | 9 | [5 empty] | 357.918
Tuesday | 10 | [5 empty] | 459.096
Wednesday | 11 | [5 empty] | 416.79
Thursday | 12 | [5 empty] | 515.328
Friday | 13 | [5 empty] | 309.804
Saturday | 14 | [5 empty] | 0
Sunday | 15 | [5 empty] | 0
Monday | 16 | [5 empty] | 114.51
Tuesday | 17 | [5 empty] | 0
Wednesday | 18 | [5 empty] | 364.584
Thursday | 19 | [5 empty] | 726.528
Friday | 20 | [5 empty] | 487.74
Saturday | 21 | [5 empty] | 0
Sunday | 22 | [5 empty] | 0
Monday | 23 | [5 empty] | 613.074
Tuesday | 24 | [5 empty] | 392.238
Wednesday | 25 | [5 empty] | 325.776
Thursday | 26 | [5 empty] | 337.788
Friday | 27 | [5 empty] | 397.782
Saturday | 28 | [5 empty] | 0
| 29 | [5 empty] | 0
| 30 | [5 empty] | 447.81
| 31 | [5 empty] | 436.392
[6 empty] | TOTAL | 8786.5692
0
Note on C4: Note: Unit of measurement

## CO2
CO2 Daily Consumption for MARCH 2026 | [7 empty] | TANK C
[6 empty] | FILLER |  | TAYLOR WHARTON CALIBRATION TANK | [5 empty] | NOT READY
DATE | FILLER Cons. (Kg.) | BMF Cons. (Kg.) | CO2 (kg.) (Ex. Vap'r Flowmeter) | CO2 (kg.) (Ex. Vap'r Calculation) | Total Prod.(HL) | CO2 ( Kg./HL) |  | inH2O | LBS_CO2 | KG_CO2 | READING Today (inH2O) |  |  | DATE | TANK C |  | TANK A | TANK B | INPUTS MOBILE(kg) | STOCK (KG) | TOTAL CONSUMPTION (KG)
[8 empty] | 10 | 722 | 327.4936 |  | POUNDS | KG |  | READING 00:30 hrs (inH2O) | QUANTITY (KG) | QUANTITY (KG) | QUANTITY (KG)
1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 2857 | 1295.9132 | 75 | 12436 | 5640.8737 | 2025-08-01 | 0 | 0 | #REF! | #REF! | #REF! | #REF!
2 | 456.92 | 112.57 | 2208.53 | 1900 | 434.742 | 4.3704 |  | 30 | 4344 | 1970.4049 |  | 12436 | 5642.4682 | 2025-08-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 360.67 | 77.13 | 2972.75 | 1700 | 405.042 | 4.1971 |  | 40 | 6143 | 2786.4175 |  |  | 2.6244 | 2025-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 388.94 | 76.23 | 2013.1 | 2700 | 419.364 | 6.4383 |  | 50 | 7941 | 3601.9764 |  |  |  | 2025-08-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 243.27 | 69.79 | 1472.31 | 1400 | 278.838 | 5.0208 |  | 60 | 9739 | 4417.5353 |  |  |  | 2025-08-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 256.27 | 157.44 | 1788.53 | 1900 | 305.8452 | 6.2123 |  | 70 | 11537 | 5233.0943 |  |  |  | 2025-08-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 |  | 80 | 13335 | 6048.6532 |  |  |  | 2025-08-07 | 0 | 0 | 0 | 0 | 0 | 0
8 | 176.59 | 78.87 | 1264.69 | 2200 | 239.58 | 9.1827 |  | 90 | 15134 | 6864.6658 |  |  |  | 2025-08-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 285.88 | 142.83 | 2110.06 | 2400 | 357.918 | 6.7054 |  | 100 | 16932 | 7680.2247 |  |  |  | 2025-08-09 | 0 | 0 | 0 | 0 | 0 | 0
10 | 267.01 | 45.27 | 3002.47 | 1700 | 459.096 | 3.7029 |  | 110 | 18730 | 8495.7836 |  |  |  | 2025-08-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 286.35 | 78.44 | 2877 | 3200 | 416.79 | 7.6777 |  | 120 | 20528 | 9311.3426 |  |  |  | 2025-08-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 372.96 | 310.71 | 3346.44 | 2500 | 515.328 | 4.8513 |  | 130 | 22326 | 10126.9015 |  |  |  | 2025-08-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 236.26 | 90.75 | 2357.72 | 2500 | 309.804 | 8.0696 |  | 140 | 24125 | 10942.914 |  |  |  | 2025-08-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 51.87 | 0 | 0 | 0 |  | 150 | 25923 | 11758.473 |  |  |  | 2025-08-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 0 | 22.06 | 25.61 | 0 | 0 | 0 |  | 160 | 27721 | 12574.0319 |  |  |  | 2025-08-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 98.07 | 58.98 | 925.83 | 800 | 114.51 | 6.9863 |  | 170 | 29519 | 13389.5909 |  |  |  | 2025-08-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 132.81 | 0 | 0 | 0 |  | 180 | 31317 | 14205.1498 |  |  |  | 2025-08-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 286.62 | 292.74 | 1687.96 | 1500 | 364.584 | 4.1143 |  | 190 | 33116 | 15021.1623 |  |  |  | 2025-08-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 409.53 | 493.18 | 3503.7 | 2300 | 726.528 | 3.1657 |  | 200 | 34914 | 15836.7213 |  |  |  | 2025-08-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 275.77 | 447.75 | 2407.84 | 2500 | 487.74 | 5.1257 |  | 210 | 36712 | 16652.2802 |  |  |  | 2025-08-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 172.64 | 438.28 | 800 | 0 | 0 |  | 220 | 38510 | 17467.8392 |  |  |  | 2025-08-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 |  | 230 | 40308 | 18283.3981 |  |  |  | 2025-08-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 375.19 | 313.34 | 2580.58 | 2000 | 613.074 | 3.2622 |  | 240 | 42107 | 19099.4106 |  |  |  | 2025-08-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 222.61 | 556.47 | 2083.8 | 2243.1818 | 392.238 | 5.7189 |  | 250 | 43905 | 19914.9696 |  |  |  | 2025-08-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 201.29 | 79.89 | 1591.15 | 1326.3636 | 325.776 | 4.0714 |  | 260 | 45703 | 20730.5285 |  |  |  | 2025-08-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 203.88 | 0 | 1258.97 | 2795.4545 | 337.788 | 8.2758 |  | 270 | 47501 | 21546.0875 |  |  |  | 2025-08-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 229.3 | 56.15 | 1499 | 1100 | 397.782 | 2.7653 |  | 280 | 49299 | 22361.6464 |  |  |  | 2025-08-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 100 | 0 | 0 |  | 290 | 51098 | 23177.6589 |  |  |  | 2025-08-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 3801 | 0 | 0 |  | 300 | 52896 | 23993.2179 |  |  |  | 2025-08-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 275.79 | 85.87 | 2105.38 | 1100 | 447.81 | 2.4564 |  | 310 | 54694 | 24808.7768 |  |  |  | 2025-08-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 248.17 | 364.1 | 1830.84 | 1200 | 436.392 | 2.7498 | TARGET | 320 | 56492 | 25624.3358 |  |  |  | 2025-08-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MTD | 6157.34 | 4183.2 | 47537.22 | 47666 | 8786.5692 | 5.4249 | 5 | 330 | 58290 | 26439.8947 |  |  |  | 2025-09-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 340 | 60089 | 27255.9072 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | 350 | 60537 | 27459.1166 | [9 empty] | TOTAL | 0

## Daily KPIs CO2
Utilities Daily Consumption
1364
2026-03-01
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | Monthly Target
Days | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Total |  | Diff.
Cases Produced |  | 6587 | 6137 | 6354 | 3969 | 4514 | 0 | 3630 | 5423 | 6956 | 6315 | 7808 | 4694 | 0 | 0 | 1735 | 0 | 5524 | 11008 | 7390 | 0 | 0 | 9289 | 5943 | 4936 | 5118 | 6027 | 0 |  |  | 0 | 119357 | 96325 | 23032
HL produced | 0 | 434.742 | 405.042 | 419.364 | 278.838 | 305.8452 | 0 | 239.58 | 357.918 | 459.096 | 416.79 | 515.328 | 309.804 | 0 | 0 | 114.51 | 0 | 364.584 | 726.528 | 487.74 | 0 | 0 | 613.074 | 392.238 | 325.776 | 337.788 | 397.782 | 0 |  |  | 0 | 7902.3672
Product Type | 0 | CB/ST | ST | ST/CB | CB/VM | VM/GN | CB | CB | CB | CB\Pscco | ST/Rose/Pscco | ST/SM | SM/GN | 0 | 0 | GN | 0 | GN/CB | CB | CB/ST | 0 | 0 | ST/CB | SH. Gin/SM |  | Bana/Ging/Grape/Sorrel | Sorrel/ST | 0 |  |  | 0
Water (m3)
Area | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | MTD
Well Supply (from filtered water) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nawasa Supply | 183 | 285 | 127 | 347 | 183 | 89 | 1 | 120 | 206 | 320 | 402 | 253 | 176 | 0 | 47 | 146 | 8 | 170 | 363 | 320 | 146 | 80 | 85 | 118 | 219 | 234 | 140 | 10 | 219 | 234 | 140 | 5371
Annanale Supply | 0 | 136 | 211 | 165 | 278 | 243 | 70 | 122 | 210 | 100 | 163 | 230 | 215 | 210 | 47 | 124 | 38 | 104 | 162 | 228 | 115 | 126 | 242 | 100 | 276 | 101 | 69 | 47 | 276 | 101 | 69 | 4578
Total Water Supply | 183 | 421 | 338 | 512 | 461 | 332 | 71 | 242 | 416 | 420 | 565 | 483 | 391 | 210 | 94 | 270 | 46 | 274 | 525 | 548 | 261 | 206 | 327 | 218 | 495 | 335 | 209 | 57 | 495 | 335 | 209 | 9949
0
Theoretical permeate | 0 | 100.74 | 165.71 | 127.02 | 212.43 | 186.88 | 54.75 | 93.44 | 161.33 | 76.65 | 124.83 | 176.66 | 163.52 | 163.52 | 163.52 | 163.52 | 163.52 | 163.52 | 124.1 | 174.47 | 88.33 | 97.09 | 183.23 | 132.13 | 157.68 | 157.68 | 157.68 | 157.68 | 157.68 | 157.68 | 0 | 4206.99 | 9809 |  | 12.4127
253.31
Permeate Produced | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 88 | 16 | 162
Service Water Plant Supply | 80 | 367 | 332 | 346 | 251 | 256 | 100 | 193 | 272 | 322 | 323 | 333 | 241 | 75 | 76 | 149 | 230 | 55 | 364 | 294 | 124 | 19 | 219 | 214 | 187 | 177 | 163 | 23 | 0 | 0 | 0 | 5785
Water consumption | 80 | 367 | 332 | 346 | 251 | 256 | 100 | 193 | 272 | 322 | 323 | 333 | 241 | 75 | 76 | 149 | 230 | 55 | 364 | 294 | 124 | 19 | 219 | 214 | 187 | 177 | 163 | 23 | 58 | 88 | 16 | 5947
|  | 8.4418 | 8.1967 | 8.2506 | 9.0016 | 8.3702 |  | 8.0558 | 7.5995 | 7.0138 | 7.7497 | 6.4619 | 7.7791 |  |  | 13.012 |  | 1.5086 | 5.0101 | 6.0278 |  |  | 3.5722 | 5.4559 | 5.7401 | 5.24 | 4.0977
Water Consumption detail | [31 empty] | 0
Brewhouse / Old Pepsi Area | 69 | 127 | 131 | 138 | 176 | 115 | 0 | 0 | 148 | 160 | 201 | 146 | 174 | 149 | 54 | 63 | 0 | 40 | 139 | 141 | 133 | 194 | 137 | 130 | 112 | 117 | 26 | 5 | 112 | 117 | 26 | 3280
Spent Grains/Wash-down Areas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.1945 | 9.9175 | 5.2541 | 30.3661
Whirlpool
Filtration/Cellars | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Processing/Cellars | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 33 | 0 | 5 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 5 | 22 | 110
CIP Process | 4 | 40 | 36 | 66 | 46 | 50 | 0 | 5 | 56 | 24 | 61 | 54 | 33 | 33 | 33 | 25 | 25 | 25 | 37 | 49 | 16 | 0 | 23 | 41 | 63 | 28 | 9 | 0 | 63 | 28 | 9 | 982 |  |  | 15588.1818
Bottles Washer | 29 | 201 | 144 | 157 | 107 | 105 | 44 | 115 | 148 | 148 | 155 | 182 | 107 | 107 | 107 | 107 | 107 | 107 | 159 | 149 | 29 | 0 | 108 | 66 | 64 | 94 | 85 | 4 | 64 | 94 | 85 | 3178
Bottle Filler | 0 | 36 | 29 | 30 | 24 | 24 | 0 | 17 | 28 | 25 | 28 | 30 | 22 | 3 | 0 | 8 | 0 | 27 | 31 | 29 | 1 | 0 | 37 | 28 | 13 | 5 | 22 | 0 | 13 | 5 | 22 | 537
Pasteuriser | 1 | 42 | 13 | 16 | 8 | 12 | 0 | 8 | 10 | 7 | 8 | 3 | 7 | 0 | 0 | 5 | 0 | 4 | 8 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156
Boiler Supply | 13 | 41 | 30 | 35 | 30 | 27 | 4 | 29 | 36 | 28 | 30 | 34 | 25 | 25 | 12 | 23 | 23 | 44 | 37 | 43 | 17 | 20 | 31 | 29 | 17 | 8 | 14 | 0 | 17 | 8 | 14 | 744
Backwash Supply | [31 empty] | 0
Refrigeration Unit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CO2 Scrubber | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160
Personnel Consumption
Total water consumption (M3) | 116 | 487 | 383 | 442 | 391 | 333 | 48 | 174 | 426 | 392 | 643 | 449 | 368 | 324 | 239 | 231 | 160 | 272 | 411 | 413 | 196 | 214 | 338 | 294 | 269 | 252 | 156 | 9 | 297.1945 | 266.9175 | 183.2541 | 9177.3661
CO2 (kg.) (Tank Gauges)
CO2 (kg.) (Ex. Vap'r) | 0 | 2208.53 | 2972.75 | 2013.1 | 1472.31 | #REF! | #REF! | 1264.69 | 2110.06 | 3002.47 | 2877 | 3346.44 | 2357.72 | 51.87 | 25.61 | 925.83 | 132.81 | 0 | 8 | 38 | 170 | 104 | 55 | 0 | 40 | 0 | 4 | 110 | 0 | 63 | 159 | #REF!
CO2 (kg.) (Filler) | 0 | 456.92 | 360.67 | 388.94 | 243.27 | 256.27 | 0 | 176.59 | 285.88 | 267.01 | 286.35 | 372.96 | 236.26 | 0 | 0 | 98.07 | 0 | 286.62 | 409.53 | 275.77 | 0 | 0 | 375.19 | 222.61 | 201.29 | 203.88 | 229.3 | 0 | 0 | 275.79 | 248.17 | 6157.34
Electricity (Kwh.) | 4566 | 7436 | 6336 | 7181 | 6442 | 6113 | 3715 | 4596 | 7348 | 6025 | 6664 | 7760 | 6030 | 4087 | 3319 | 3950 | 2693 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 158468
Fuel (L) | 1980 | 3750 | 3270 | 3790 | 3410 | 2920 | 430 | 2380 | 3380 | 3740 | 3480 | 3760 | 3240 | 1730 | 1550 | 2110 | 710 | 2730 | 2730 | 2730 | 2730 | 2730 | 2730 | 2730 | 2730 | 2730 | 2730 | 2730 | 2730 | 2730 | 2730 | 83850
Water (m3)
Area | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 9 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | MTD | Target | Diff
Total water consumption |  | 9.6839 | 8.3448 | 12.209 | 16.5329 | 10.8552 |  | 10.101 | 11.6228 | 9.1484 | 13.556 | 9.3727 | 12.6209 |  |  | 23.5787 |  | 7.5154 | 7.2261 | 11.2355 |  |  | 5.3338 | 5.5579 | 15.1945 | 9.9175 | 5.2541 |  |  |  |  | 12.5899 | 10.2 | -2.3899
Consumption detail | [31 empty] | MTD | Target | Diff
Brewhouse / Old Pepsi Area |  | 2.9213 | 3.2342 | 3.2907 | 6.3119 | 3.7601 |  | 0 | 4.135 | 3.4851 | 4.8226 | 2.8331 | 5.6165 |  |  | 5.5017 |  | 1.0971 | 1.9132 | 2.8909 |  |  | 2.2346 | 3.3143 | 3.4379 | 3.4637 | 0.65362 |  |  |  |  | 4.1507 | 2.5 | -1.6507
Brewhouse (Hls brewed) | 2.103 | 8.5869 | 3.2758 | 3.1236 | 4.4512 | 3.8747 |  |  | 3.7813 | 3.4685 | 4.527 | 3.2743 | 3.4835 | 3.3756 | 10.9091 | 3.1947 |  | 4.0363 | 3.0429 | 2.7105 | 3.5839 | 6.0987 | 2.9972 | 3.2427 | 2.847 | 6.0969 | 5.3279 |  |  | 8.0247 |  | 3.9313 | 2.5 | -1.4313
Spent Grains/Wash-down Areas |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.038427 | 0.1 | 0.061573
Whirlpool | [32 empty] | 0.1 | 0.1
Filtration/Cellars | Mon: 0; Tue: 0; Wed: 0; Thu: 0; Fri: 0; Sun: 0; Mon: 0; Tue: 0; Wed: 0; Thu: 0; Fri: 0; Mon: 0; Wed: 0; Thu: 0; Fri: 0 | 0 | 0.7 | 0.7
Processing/Cellars |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 0.68571 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.1392 | 1 | 0.8608
CIP Process |  | 0.92009 | 0.8888 | 1.5738 | 1.6497 | 1.6348 |  | 0.2087 | 1.5646 | 0.52277 | 1.4636 | 1.0479 | 1.0652 |  |  | 2.1832 |  | 0.68571 | 0.50927 | 1.0046 |  |  | 0.37516 | 1.0453 | 1.9338 | 0.82892 | 0.22625 |  |  |  |  | 1.2427 | 0.7 | -0.54267
Bottles Washer |  | 4.6234 | 3.5552 | 3.7438 | 3.8374 | 3.4331 |  | 4.8001 | 4.135 | 3.2237 | 3.7189 | 3.5317 | 3.4538 |  |  | 9.3442 |  | 2.9349 | 2.1885 | 3.0549 |  |  | 1.7616 | 1.6827 | 1.9645 | 2.7828 | 2.1368 |  |  |  |  | 4.0216 | 2.6 | -1.4216
Bottle Washer | [32 empty] | 2.6 | 2.6
Bottle Filler |  | 0.82808 | 0.71598 | 0.71537 | 0.86071 | 0.78471 |  | 0.70958 | 0.7823 | 0.54455 | 0.6718 | 0.58215 | 0.71013 |  |  | 0.69863 |  | 0.74057 | 0.42669 | 0.59458 |  |  | 0.60352 | 0.71385 | 0.39905 | 0.14802 | 0.55307 |  |  |  |  | 0.67954 | 0.7 | 0.020457
Pasteuriser |  | 0.96609 | 0.32095 | 0.38153 | 0.2869 | 0.39236 |  | 0.33392 | 0.27939 | 0.15247 | 0.19194 | 0.058215 | 0.22595 |  |  | 0.43664 |  | 0.10971 | 0.11011 | 0.041005 |  |  | 0.032622 | 0 | 0 | 0 | 0 |  |  |  |  | 0.19741 | 0.1 | -0.097409
Boiler Supply |  | 0.94309 | 0.74066 | 0.8346 | 1.0759 | 0.8828 |  | 1.2105 | 1.0058 | 0.60989 | 0.71979 | 0.65977 | 0.80696 |  |  | 2.0086 |  | 1.2069 | 0.50927 | 0.88162 |  |  | 0.50565 | 0.73935 | 0.52183 | 0.23683 | 0.35195 |  |  |  |  | 0.94149 | 0.6 | -0.34149
Backwash Supply |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0.5 | 0.5
Refrigeration Unit |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0.3 | 0.3
CO2 Scrubber | [32 empty] | 0.4 | 0.4
Personnel Consumption | [32 empty] | 0.2 | 0.2
Water consumption (M3) | 2.103 | 19.7889 | 12.7316 | 13.6634 | 18.4737 | 14.7625 | 0 | 7.2627 | 15.6835 | 12.007 | 16.1156 | 11.9872 | 15.362 | 3.3756 | 10.9091 | 23.3676 | 0 | 11.4969 | 8.6999 | 11.1781 | 3.5839 | 6.0987 | 8.5104 | 10.7382 | 11.1042 | 13.5572 | 9.2496 | 0 | 0 | 8.0247 | 0 | 15.3423 | 15.6 | 0.25773
Bottling Hall water | 0 | 6.4176 | 4.5921 | 4.8407 | 4.985 | 4.6102 | 0 | 5.8436 | 5.1967 | 3.9207 | 4.5826 | 4.1721 | 4.3899 | 0 | 0 | 10.4794 | 0 | 3.7851 | 2.7253 | 3.6905 | 0 | 0 | 2.3978 | 2.3965 | 2.3636 | 2.9308 | 2.6899 | 0 | 0 | 0 | 0 | 4.8985 | 6 | 1.1015
CO2 (kg./Hl.) KPI |  | 5.0801 | 7.3394 | 4.8004 | 5.2802 | #REF! |  | 5.2788 | 5.8954 | 6.54 | 6.9028 | 6.4938 | 7.6104 |  |  | 8.0851 |  | 0 | 0.011011 | 0.07791 |  |  | 0.089712 | 0 | 0.12278 | 0 | 0.010056 |  |  |  |  | #REF! | 5 | #REF!
CO2 Filler (kg./Hl.) KPI |  | 1.051 | 0.89045 | 0.92745 | 0.87244 | 0.83791 |  | 0.73708 | 0.79873 | 0.5816 | 0.68704 | 0.72373 | 0.76261 |  |  | 0.85643 |  | 0.78616 | 0.56368 | 0.5654 |  |  | 0.61198 | 0.56754 | 0.61788 | 0.60357 | 0.57645 |  |  |  |  | 0.77918 | 1.7 | 0.92082
Electricity (Kwh./Hl.) KPI |  | 17.1044 | 15.6428 | 17.1235 | 23.103 | 19.9872 |  | 19.1836 | 20.5298 | 13.1236 | 15.9889 | 15.0584 | 19.4639 |  |  | 34.4948 |  | 16.01 | 8.0341 | 11.9674 |  |  | 9.5209 | 14.8813 | 17.9172 | 17.2801 | 14.6739 |  |  |  |  | 20.0532 | 22 | 1.9468
[33 empty] | 31.2 | 31.2
Fuel (L/Hl.) KPI |  | 8.6258 | 8.0732 | 9.0375 | 12.2293 | 9.5473 |  | 9.9341 | 9.4435 | 8.1464 | 8.3495 | 7.2963 | 10.4582 |  |  | 18.4263 |  | 7.488 | 3.7576 | 5.5972 |  |  | 4.453 | 6.9601 | 8.38 | 8.082 | 6.8631 |  |  |  |  | 10.6107 | 7.2 | -3.4107
Total Bottles Washed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | .
CO2 to Liqufier (kg.) | 0 | 112.57 | 77.13 | 76.23 | 69.79 | 157.44 | 324967.25 | 0 | 142.83 | 45.27 | 78.44 | 310.71 | 90.75 | 0 | 22.06 | 58.98 | 0 | 292.74 | 493.18 | 447.75 | 172.64 | 0 | 313.34 | 556.47 | 79.89 | 0 | 56.15 | 0 | 0 | 85.87 | 364.1 | 329071.58
CO2 recovered (Kg - liquid) | [31 empty] | 0
CO2 liquid conversion efficiency | [31 empty] | 0% | bar: Mon to Sat; Mon to Fri; Sun to Mon; Wed to Sat; Mon to Wed; Fri; Mon to Tue
Water Recovered (m3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tanks on Collection
Hls Brewed | 328.1 | 147.9 | 399.9 | 441.8 | 395.4 | 296.8 | 0 | 0 | 391.4 | 461.3 | 444 | 445.9 | 499.5 | 441.4 | 49.5 | 197.2 | 0 | 99.1 | 456.8 | 520.2 | 371.1 | 318.1 | 457.1 | 400.9 | 393.4 | 191.9 | 48.8 | 0 | 0 | 145.8 | 0 | 8343.3
Product | VM | GU | GU/CB | CB | CB | VM/GN | 0 | 0 | ST | SM | ST/CB | CB | CB | CB/ST | ST | CB | 0 | CB | CB | CB/ST | ST | SM | SM/CB | CB | CB/VM | VM | CB | 0 | 0 | ST | 0
No. of Brews | 7 | 3 | 8 | 9 | 8 | 6 | 0 | 0 | 8 | 9 | 9 | 9 | 10 | 9 | 2 | 4 | 0 | 2 | 9 | 10 | 7 | 6 | 9 | 8 | 8 | 4 | 1 | 0 | 0 | 3 | 0 | 168
Raw Water In - Nawasa | 0 | 138 | 227 | 174 | 291 | 256 | 75 | 128 | 221 | 105 | 171 | 242 | 224 | 224 | 224 | 224 | 224 | 224 | 170 | 239 | 121 | 133 | 251 | 181 | 216 | 216 | 216 | 216 | 216 | 216 | 0 | 5763
Into RO | [31 empty] | 0 | bar: Sun
| 4566 | 7436 | 6336 | 7181 | 6442 | 6113 | 3715 | 4596 | 7348 | 6025 | 6664 | 7760 | 6030 | 4087 | 3319 | 3950 | 2693 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 5837 | 158468
Note on A79: RAntoine: Line deleted by MD on April 20, 2011. Do not reinsert

## Daily KPIs
Utilities Daily Consumption
1904-12-04
2026-03-01 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  |  | Monthly Target
| Sunday | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday | Monday | Tuesday | Wednesday | Thursday | Friday | Saturday | Sunday | Monday | Tuesday |  | Total |  | Diff.
Cases Produced |  | 6587 | 6137 | 6354 | 3969 | 4514 |  | 3630 | 5423 | 6956 | 6315 | 7808 | 4694 |  |  | 1735 | 0 | 5524 | 11008 | 7390 |  |  | 9289 | 5943 | 4936 | 5118 | 6027 |  |  | 6785 | 6612 | 792 | 133546 | 146375 | -12829
HL produced |  | 434.742 | 405.042 | 419.364 | 278.838 | 305.8452 |  | 239.58 | 357.918 | 459.096 | 416.79 | 515.328 | 309.804 | 0 | 0 | 114.51 | 0 | 364.584 | 726.528 | 487.74 |  |  | 613.074 | 392.238 | 325.776 | 337.788 | 397.782 |  |  | 447.81 | 436.392 | 52.272 | 8838.8412
Product Type |  | CB/ST | ST | ST/CB | CB/VM | VM/GN |  | CB | CB | CB\Pscco | ST/Rose/Pscco | ST/SM | SM/GN |  |  | GN |  | GN/CB | CB | CB/ST |  |  | ST/CB | SH. Gin/SM | SM/Csoda/Kola/Cream | Bana/Ging/Grape/Sorrel | Sorrel/ST |  |  | CB | CB/VM | kegs
Hls Brewed | 328.1 | 147.9 | 399.9 | 441.8 | 395.4 | 296.8 |  |  | 391.4 | 461.3 | 444 | 445.9 | 499.5 | 441.4 | 49.5 | 197.2 |  | 99.1 | 456.8 | 520.2 | 371.1 | 318.1 | 457.1 | 400.9 | 393.4 | 191.9 | 48.8 |  |  | 145.8 | 502.8 |  | 8846.1
Product | VM | GU | GU/CB | CB | CB | CB/ST |  |  | ST | SM | ST/CB | CB | CB | CB/ST | ST | CB |  | CB | CB | CB/ST | ST | SM | SM/CB | CB | CB/VM | VM | CB |  |  | ST | ST/CB
No. of Brews | 7 | 3 | 8 | 9 | 8 | 6 |  |  | 8 | 9 | 9 | 9 | 10 | 9 | 2 | 4 |  | 2 | 9 | 10 | 7 | 6 | 9 | 8 | 8 | 4 | 1 |  |  | 3 | 10 |  | 178
Brewhouse (Hls brewed) | 2.103 | 8.5869 | 3.2758 | 3.1236 | 4.4512 | 3.8747 |  |  | 3.7813 | 3.4685 | 4.527 | 3.2743 | 3.4835 | 3.3756 | 10.9091 | 3.1947 |  | 4.0363 | 3.0429 | 2.7105 | 3.5839 | 6.0987 | 2.9972 | 3.2427 | 2.847 | 6.0969 | 5.3279 |  |  | 3.7037 | 2.2673 |  | 3.6095
Water (m3)
MTD
Well Supply (from filtered water) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Nawasa Supply | 183 | 285 | 127 | 347 | 183 | 89 | 1 | 120 | 206 | 320 | 402 | 253 | 176 | 0 | 47 | 146 | 8 | 170 | 363 | 320 | 146 | 80 | 85 | 118 | 219 | 234 | 140 | 10 | 0 | 191 | 242 |  | 5211
Annanale Supply | 0 | 136 | 211 | 165 | 278 | 243 | 70 | 122 | 210 | 100 | 163 | 230 | 215 | 210 | 47 | 124 | 38 | 104 | 162 | 228 | 115 | 126 | 242 | 100 | 276 | 101 | 69 | 47 | 0 | 189 | 83 |  | 4404
Total Water Supply | 183 | 421 | 338 | 512 | 461 | 332 | 71 | 242 | 416 | 420 | 565 | 483 | 391 | 210 | 94 | 270 | 46 | 274 | 525 | 548 | 261 | 206 | 327 | 218 | 495 | 335 | 209 | 57 | 0 | 380 | 325 |  | 9615
0
Theoretical permeate | 0 | 100.74 | 165.71 | 127.02 | 212.43 | 186.88 | 54.75 | 93.44 | 161.33 | 76.65 | 124.83 | 176.66 | 163.52 | 161.33 | 37.23 | 94.17 | 29.2 | 80.3 | 124.1 | 174.47 | 88.33 | 97.09 | 183.23 | 132.13 | 157.68 | 76.65 | 53.29 | 35.04 | 0 | 144.54 | 63.51 |  | 3376.25 | 10024 |  | 11.3409
253.31
Permeate Produced | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Service Water Plant Supply | 80 | 367 | 332 | 346 | 251 | 256 | 100 | 193 | 272 | 322 | 323 | 333 | 241 | 75 | 76 | 149 | 230 | 55 | 364 | 294 | 124 | 19 | 219 | 214 | 187 | 177 | 163 | 23 | 0 | 317 | 0 |  | 6102
Brewhouse | 69 | 127 | 131 | 138 | 176 | 115 | 0 | 0 | 148 | 160 | 201 | 146 | 174 | 149 | 54 | 63 | 0 | 40 | 139 | 141 | 133 | 194 | 137 | 130 | 112 | 117 | 26 | 5 | 0 | 54 | 114 |  | 3193
Boiler Supply | 13 | 41 | 30 | 35 | 30 | 27 | 4 | 29 | 36 | 28 | 30 | 34 | 25 | 10 | 12 | 23 | 16 | 44 | 37 | 43 | 17 | 20 | 31 | 29 | 17 | 8 | 14 | 0 | 0 | 30 | 16 |  | 729
Water consumption | 162 | 535 | 493 | 519 | 457 | 398 | 104 | 222 | 456 | 510 | 554 | 513 | 440 | 234 | 142 | 235 | 246 | 139 | 540 | 478 | 274 | 233 | 387 | 373 | 316 | 302 | 203 | 28 | 0 | 401 | 130 |  | 10024
Water Consumption detail
Brewhouse | 69 | 127 | 131 | 138 | 176 | 115 | 0 | 0 | 148 | 160 | 201 | 146 | 174 | 149 | 54 | 63 | 0 | 40 | 139 | 141 | 133 | 194 | 137 | 130 | 112 | 117 | 26 | 5 | 0 | 54 | 114 |  | 3193
Spent grains/wash-down area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Whirlpool
Cellars/Filtration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Processing/Cellars | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
CIP Process | 4 | 40 | 36 | 66 | 46 | 50 | 0 | 5 | 56 | 24 | 61 | 54 | 33 | 30 | 5 | 25 | 0 | 63 | 37 | 49 | 16 | 0 | 23 | 41 | 63 | 28 | 9 | 0 | 0 | 68 | 38 |  | 970
Bottles Washer | 29 | 201 | 144 | 157 | 107 | 105 | 44 | 115 | 148 | 148 | 155 | 182 | 107 | 2 | 50 | 54 | 1 | 159 | 159 | 149 | 29 | 0 | 108 | 66 | 64 | 94 | 85 | 4 | 0 | 146 | 107 |  | 2919
Bottle Filler | 0 | 36 | 29 | 30 | 24 | 24 | 0 | 17 | 28 | 25 | 28 | 30 | 22 | 3 | 0 | 8 | 0 | 27 | 31 | 29 | 1 | 0 | 37 | 28 | 13 | 5 | 22 | 0 | 0 | 24 | 29 |  | 550
Pasteuriser | 1 | 42 | 13 | 16 | 8 | 12 | 0 | 8 | 10 | 7 | 8 | 3 | 7 | 0 | 0 | 5 | 0 | 4 | 8 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 |  | 159
Boiler Supply | 13 | 41 | 30 | 35 | 30 | 27 | 4 | 29 | 36 | 28 | 30 | 34 | 25 | 10 | 12 | 23 | 16 | 44 | 37 | 43 | 17 | 20 | 31 | 29 | 17 | 8 | 14 | 0 | 0 | 30 | 16 |  | 729
Refrigeration Unit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
CO2 Scrubber | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Personnel Consumption
Backwash Supply | [32 empty] | 0
Total water consumption (M3) | 116 | 487 | 383 | 442 | 391 | 333 | 48 | 174 | 426 | 392 | 483 | 449 | 368 | 194 | 121 | 178 | 17 | 337 | 411 | 413 | 196 | 214 | 338 | 294 | 269 | 252 | 156 | 9 | 0 | 323 | 306 |  | 8520
Consumption detail | [32 empty] | MTD | Target | Diff
Brewhouse/Filtration/Cellar |  | 2.9213 | 3.2342 | 3.2907 | 6.3119 | 3.7601 |  | 0 | 4.135 | 3.4851 | 4.8226 | 2.8331 | 5.6165 |  |  | 5.5017 |  | 1.0971 | 1.9132 | 2.8909 |  |  | 2.2346 | 3.3143 | 3.4379 | 3.4637 | 0.65362 |  |  | 1.2059 | 2.6123 |  | 3.6125 | 3.2 | -0.41246
Spent Grains/Wash-down Areas | [32 empty] | 0 | 0.1 | 0.1
Whirlpool |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 0.1 | 0.1
Cellars/Filtration |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 0.7 | 0.7
Processing/Cellars |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 1 | 1
CIP Process |  | 0.92009 | 0.8888 | 1.5738 | 1.6497 | 1.6348 |  | 0.2087 | 1.5646 | 0.52277 | 1.4636 | 1.0479 | 1.0652 |  |  | 2.1832 |  | 1.728 | 0.50927 | 1.0046 |  |  | 0.37516 | 1.0453 | 1.9338 | 0.82892 | 0.22625 |  |  | 1.5185 | 0.87078 |  | 1.0974 | 0.7 | -0.39743
Bottles Washer |  | 4.6234 | 3.5552 | 3.7438 | 3.8374 | 3.4331 |  | 4.8001 | 4.135 | 3.2237 | 3.7189 | 3.5317 | 3.4538 |  |  | 4.7157 |  | 4.3611 | 2.1885 | 3.0549 |  |  | 1.7616 | 1.6827 | 1.9645 | 2.7828 | 2.1368 |  |  | 3.2603 | 2.4519 |  | 3.3025 | 2.1 | -1.2025
Bottle Filler |  | 0.82808 | 0.71598 | 0.71537 | 0.86071 | 0.78471 |  | 0.70958 | 0.7823 | 0.54455 | 0.6718 | 0.58215 | 0.71013 |  |  | 0.69863 |  | 0.74057 | 0.42669 | 0.59458 |  |  | 0.60352 | 0.71385 | 0.39905 | 0.14802 | 0.55307 |  |  | 0.53594 | 0.66454 |  | 0.62225 | 0.7 | 0.077746
Pasteuriser |  | 0.96609 | 0.32095 | 0.38153 | 0.2869 | 0.39236 |  | 0.33392 | 0.27939 | 0.15247 | 0.19194 | 0.058215 | 0.22595 |  |  | 0.43664 |  | 0.10971 | 0.11011 | 0.041005 |  |  | 0.032622 | 0 | 0 | 0 | 0 |  |  | 0.022331 | 0.04583 |  | 0.17989 | 0.1 | -0.079888
Boiler Supply |  | 0.94309 | 0.74066 | 0.8346 | 1.0759 | 0.8828 |  | 1.2105 | 1.0058 | 0.60989 | 0.71979 | 0.65977 | 0.80696 |  |  | 2.0086 |  | 1.2069 | 0.50927 | 0.88162 |  |  | 0.50565 | 0.73935 | 0.52183 | 0.23683 | 0.35195 |  |  | 0.66993 | 0.36664 |  | 0.82477 | 0.6 | -0.22477
Backwash Supply | [33 empty] | 0.5 | 0.5
Refrigeration Unit |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 0.3 | 0.3
CO2 Scrubber | [33 empty] | 0.4 | 0.4
Personnel Consumption | [33 empty] | 0.2 | 0.2
Water consumption (M3) | 0 | 11.202 | 9.4558 | 10.5398 | 14.0225 | 10.8879 | 0 | 7.2627 | 11.9022 | 8.5385 | 11.5886 | 8.7129 | 11.8785 | 0 | 0 | 15.5445 | 0 | 9.2434 | 5.657 | 8.4676 | 0 | 0 | 5.5132 | 7.4954 | 8.2572 | 7.4603 | 3.9217 | 0 | 0 | 7.2129 | 7.012 |  | 9.6393 | 9.6 | -0.039273
Bottling Hall water | 0 | 6.4176 | 4.5921 | 4.8407 | 4.985 | 4.6102 | 0 | 5.8436 | 5.1967 | 3.9207 | 4.5826 | 4.1721 | 4.3899 | 0 | 0 | 5.851 | 0 | 5.2114 | 2.7253 | 3.6905 | 0 | 0 | 2.3978 | 2.3965 | 2.3636 | 2.9308 | 2.6899 | 0 | 0 | 3.8186 | 3.1623 |  | 4.1046 | 2.9 | -1.2046
Water Plant Total (Before Sand Filter) | 0 | 138 | 227 | 174 | 291 | 256 | 75 | 128 | 221 | 105 | 171 | 242 | 224 | 221 | 51 | 129 | 40 | 110 | 170 | 239 | 121 | 133 | 251 | 181 | 216 | 105 | 73 | 48 | 0 | 198 | 87 |  | 4625
CO2 (kg.) Filler | [32 empty] | 0
CO2 (kg.) (Ex. Vap'r) | 0 | 1900 | 1700 | 2700 | 1400 | 1900 | 0 | 2200 | 2400 | 1700 | 3200 | 2500 | 2500 |  |  | 800 | 0 | 1500 | 2300 | 2500 | 800 |  | 2000 | 2243.1818 | 1326.3636 | 2795.4545 | 1100 | 100 | 3801 | 1100 | 1200 |  | 47666
CO2 Totalizer | 0 | 2208.53 | 2972.75 | 2013.1 | 1472.31 | 1788.53 | 0 | 1264.69 | 2110.06 | 3002.47 | 2877 | 3346.44 | 2357.72 | 51.87 | 25.61 | 925.83 | 132.81 | 1687.96 | 3503.7 | 2407.84 | 438.28 | 0 | 2580.58 | 2083.8 | 1591.15 | 1258.97 | 1499 | 0 | 0 | 2105.38 | 1830.84 |  | 47537.22
CO2 (kg.) (Filler) | 0 | 456.92 | 360.67 | 388.94 | 243.27 | 256.27 | 0 | 176.59 | 285.88 | 267.01 | 286.35 | 372.96 | 236.26 | 0 | 0 | 98.07 | 0 | 286.62 | 409.53 | 275.77 | 0 | 0 | 375.19 | 222.61 | 201.29 | 203.88 | 229.3 | 0 | 0 | 275.79 | 248.17 |  | 6157.34
CO2 (kg.) (FILTRATION) | 0 | 112.57 | 77.13 | 76.23 | 69.79 | 157.44 | 0 | 78.87 | 142.83 | 45.27 | 78.44 | 310.71 | 90.75 | 0 | 22.06 | 58.98 | 0 | 292.74 | 493.18 | 447.75 | 172.64 | 0 | 313.34 | 556.47 | 79.89 | 0 | 56.15 | 0 | 0 | 85.87 | 364.1 |  | 4183.2
0
CO2 (kg.)Consumption Meter | 0 | 2208.53 | 2972.75 | 2013.1 | 1472.31 | #REF! | #REF! | 1264.69 | 2110.06 | 3002.47 |  | 3346.44 |  | 51.87 | 25.61 | 925.83 | 132.81 | 0 | 8 | 38 | 170 | 104 | 55 | 0 | 40 | 0 | 4 | 110 | 159 | #REF! | 0
Electricity GRENLEC (Kwh.) | 4566 | 7436 | 6336 | 7181 | 6442 | 6113 | 3715 | 4596 | 7348 | 6025 | 6664 | 7760 | 6030 | 4087 | 3319 | 3950 | 2693 | 5837 | 5522 | 6127 | 3710 | 3675 | 7166 | 5644 | 6333 | 6354 | 4663 | 2858 | 2785 | 5188 | 6585 |  | 166708
| #VALUE! | [31 empty] | #VALUE!
| 7813.5 | 8789.8 | 7771.1 | 7445.2 | 5184.7 | 6151.3 | 9036.7 | 7643 | 8121 | 8810.1 | 7716.1 | 5745 | 4684.1 | 5616.2 | 4253.7 | 7360.6 | 7147.4 | 7710.2 | 5427.9 | 5445.6 | 8591.4 | 7234.1 | 7732.2 | 779440% | 621640% | 4304.6 | 2785 | 5188 | 6585 | 209145.8 | 0 |  | 403450.1
Elec PV System (Kwh.) Tar. 1493 (Kwh) | 1593.9 | 1245.6 | 1477.5 | 1608.8 | 1329.1 | 1332.2 | 1469.7 | 1555.3 | 1688.7 | 1618 | 1457 | 1050.1 | 1686.1 | 1658 | 1365.1 | 1666.2 | 1560.7 | 1523.6 | 1625.4 | 1583.2 | 1717.9 | 1770.6 | 1425.4 | 1590.1 | 1399.2 | 1440.4 | 1553.4 | 1446.6 | 1541.6 | 1369.8 | 1201.7 |  | 46550.9
Fuel (L) | 1980 | 3750 | 3270 | 3790 | 3410 | 2920 | 430 | 2380 | 3380 | 3740 | 3480 | 3760 | 3240 | 1730 | 1550 | 2110 | 710 | 2730 | 4150 | 3480 | 1670 | 2120 | 3890 | 3210 | 2450 | 2240 | 2200 | 0 | 0 | 3700 | 3160 |  | 80630
Steam Mass Flow | 0 | 0 | 0 | 0 | 0 | 0 | 142.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.288 | 0 | 0 | 0 | 0 | 0 | 112.135 | 10.012 | 688.734 | 785.391 | 0 | 0 | 624.876 | 0 | 0 | 609.309 | 32.589 |  | 3120.528
Water (m3)
Area | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 |  | MTD | Target | Diff | %
Total water consumption |  | 9.6839 | 8.3448 | 12.209 | 16.5329 | 10.8552 |  | 10.101 | 11.6228 | 9.1484 | 13.556 | 9.3727 | 12.6209 |  |  | 23.5787 |  | 7.5154 | 7.2261 | 11.2355 |  |  | 5.3338 | 5.5579 | 15.1945 | 9.9175 | 5.2541 |  |  | 8.4857 | 7.4474 |  | 10.8781 | 10.2 | -0.67812 | 106.6483
[33 empty] | 0 |  |  | #DIV/0!
CO2 (kg./Hl.) KPI |  | 4.3704 | 4.1971 | 6.4383 | 5.0208 | 6.2123 |  | 9.1827 | 6.7054 | 3.7029 | 7.6777 | 4.8513 | 8.0696 |  |  | 6.9863 |  | 4.1143 | 3.1657 | 5.1257 |  |  | 3.2622 | 5.7189 | 4.0714 | 8.2758 | 2.7653 |  |  | 2.4564 | 2.7498 |  | 5.3928 | 5 | -0.39279 | 107.8558
CO2 Filler (kg./Hl.) KPI |  | 1.051 | 0.89045 | 0.92745 | 0.87244 | 0.83791 |  | 0.73708 | 0.79873 | 0.5816 | 0.68704 | 0.72373 | 0.76261 |  |  | 0.85643 |  | 0.78616 | 0.56368 | 0.5654 |  |  | 0.61198 | 0.56754 | 0.61788 | 0.60357 | 0.57645 |  |  | 0.61586 | 0.56869 |  | 0.69662 | 1.7 | 1.0034 | 40.9778
Electricity (Kwh./Hl.) KPI |  | 19.9695 | 19.2906 | 20.9598 | 27.8696 | 24.343 |  | 25.6753 | 25.248 | 16.6479 | 19.4846 | 17.0961 | 24.9064 |  |  | 49.0455 |  | 20.189 | 9.8377 | 15.808 |  |  | 14.0136 | 18.4431 | 23.7347 | 23.0748 | 15.6277 |  |  | 14.6442 | 17.8434 |  | 24.1275 | 22 | -2.1275 | 109.6703
[33 empty] | 0 |  |  | #DIV/0!
Fuel (L/Hl.) KPI |  | 8.6258 | 8.0732 | 9.0375 | 12.2293 | 9.5473 |  | 9.9341 | 9.4435 | 8.1464 | 8.3495 | 7.2963 | 10.4582 |  |  | 18.4263 |  | 7.488 | 5.7121 | 7.1349 |  |  | 6.3451 | 8.1838 | 7.5205 | 6.6314 | 5.5307 |  |  | 8.2624 | 7.2412 |  | 9.1222 | 7.2 | -1.9222 | 126.6977
Total Bottles Washed | [32 empty] | 0 |  | .
Bottle Washer (Including rejects) | [32 empty] | #DIV/0! | 2.6 | #DIV/0!
CO2 to Liqufier (kg.) | 0 | 112.57 | 77.13 | 76.23 | 69.79 | 157.44 | 324967.25 | 0 | 142.83 | 45.27 | 78.44 | 310.71 | 90.75 | 0 | 22.06 | 58.98 | 0 | 292.74 | 493.18 | 447.75 | 172.64 | 0 | 313.34 | 556.47 | 79.89 | 0 | 56.15 | 0 | #REF! | #REF! | 85.87 |  | #REF!
CO2 recovered (Kg - liquid) | [32 empty] | 0
CO2 liquid conversion efficiency |  | 0% | 0% | 0% | 0% |  | 0% |  | 0% | 0% | 0% | 0% | 0% |  | 0% | 0% |  | 0% | 0% | 0% | 0% |  | 0% | 0% | 0% |  | 0% |  | #REF! | #REF! | 0% |  | #REF!
Water Recovered (m3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | 0 |  | #REF!
Tanks on Collection
Into RO | _ | 138 | [24 empty] | _ | _ |  |  | _ |  | 138
| 4566 |  | 6336 | 7181 | 6442 | 6113 | 3715 | 4596 | 7348 | 6025 | 6664 | 7760 | 6030 | 4087 | 3319 | 3950 | 2693 | 5837 | 5522 | 6127 | 3710 | 3675 | 7166 | 5644 | 6333 | 6354 | 4663 | 2858 | 2785 | 5188 | 6585 |  | 166708
7436
[33 empty] | 21.8284 | %
Note on S14: Kaylil Baptiste: Tank availability
Note on A69: RAntoine: Line deleted by MD on April 20, 2011. Do not reinsert
Note on B74: Tank A 11000 kgs Tank B 0 kgs Tank C 23200Kgs mobile approx 0 Kgs
Note on C74: Tank A 11000 kgs Tank B 0 kgs Tank C 23200Kgs mobile approx 0 Kgs
Note on D74: Tank A 9100 kgs Tank B 0 kgs Tank C 23200Kgs mobile approx 0 Kgs
Note on E74: Tank A 7400 kgs Tank B 0 kgs Tank C 23200Kgs mobile approx 0 Kgs
Note on F74: Tank A 4700 kgs Tank B 0 kgs Tank C 23200Kgs mobile approx 0 Kgs
Note on G74: Tank A 3300 kgs Tank B 0 kgs Tank C 23200Kgs mobile approx 0 Kgs
Note on H74: Tank A 1400 kgs Tank B 0 kgs Tank C 23200Kgs mobile approx 0 Kgs
Note on I74: Tank A 1400 kgs Tank B 0 kgs Tank C 23200Kgs mobile approx 0 Kgs
Note on J74: Tank A 0 kgs Tank B 0 kgs Tank C 22400Kgs mobile approx 0 Kgs
Note on K74: Tank A 0 kgs Tank B 0 kgs Tank C 20000Kgs mobile approx 0 Kgs
Note on L74: Tank A 0 kgs Tank B 0 kgs Tank C 18300Kgs mobile approx 0 Kgs
Note on M74: Tank A 0 kgs Tank B 0 kgs Tank C 15100Kgs mobile approx 0 Kgs
Note on N74: Tank A 0 kgs Tank B 0 kgs Tank C 12600 Kgs mobile approx 0 Kgs
Note on O74: Tank A 0 kgs Tank B 0 kgs Tank C 10100 Kgs mobile approx 0 Kgs
Note on P74: Tank A 0 kgs Tank B 0 kgs Tank C 10100 Kgs mobile approx 0 Kgs
Note on Q74: Tank A 0 kgs Tank B 0 kgs Tank C 10100 Kgs mobile approx 0 Kgs
Note on R74: Tank A 0 kgs Tank B 0 kgs Tank C 9300 Kgs mobile approx 16900 Kgs
Note on S74: Tank A 0 kgs Tank B 0 kgs Tank C 9300 Kgs mobile approx 16900 Kgs
Note on T74: Tank A 11300 kgs Tank B 0 kgs Tank C 13400 Kgs mobile approx 00 Kgs
Note on U74: Tank A 10600 kgs Tank B 0 kgs Tank C11800 Kgs mobile approx 0 Kgs
Note on V74: Tank A 10600 kgs Tank B 0 kgs Tank C 9300 Kgs mobile approx 0 Kgs
Note on W74: Tank A 10600 kgs Tank B 0 kgs Tank C 8500 Kgs mobile approx 0 Kgs
Note on X74: Tank A 10600 kgs Tank B 0 kgs Tank C 8500 Kgs mobile approx 0 Kgs
Note on Y74: Tank A 10100 kgs Tank B 0 kgs Tank C 6500 Kgs mobile approx 19600 Kgs
Note on Z74: Tank A 10600 kgs Tank B 0 kgs Tank C 5200 Kgs mobile approx 19600 Kgs
Note on AA74: Tank A 9300 kgs Tank B 0kgs Tank C 17,505 Kgs mobile approx 19600 Kgs
Note on AB74: Tank A 8200 kgs Tank B 0kgs Tank C 17,505 Kgs mobile approx 19600 Kgs
Note on AC74: Tank A 8100 kgs Tank B 0kgs Tank C 17,505 Kgs mobile approx 19600Kgs
Note on AD74: Tank A 8100 kgs Tank B 0kgs Tank C 17,505 Kgs mobile approx 19600Kgs 3801kgs - losses
Note on AE74: Tank A 8100 kgs Tank B 0kgs Tank C 17,505 Kgs mobile approx 19600 Kgs
Note on AF74: Tank A 7000 kgs Tank B 0kgs Tank C 17,505 Kgs mobile approx 19600Kgs
Note on AG74: Tank A 5800 kgs Tank B 0kgs Tank C 17,505 Kgs mobile approx 16900Kgs
Note on K75: Alexander Dominguez-Ramon: New configuration parameters have been adjusted on Totalizer Flowmeter Prowirl R200 (density, temperature) 4:00 PM
Note on AE75: Alexander Dominguez-Ramon: Reading Ne Flowmeter
Note on L80: Alexander Dominguez-Ramon: Yesterday 2/11/2026 the Setpoint of the RU2 Hanbell Screw Compressor was setted at -2 °C at 8:30 am. Temperature On: 0 °C Temperature Off: -2 °C

## Water Analysis. '26
DAILY WATER CONSUMPTION FOR JANUARY 2026
| Nawasa | Nawasa Daily | Service Water | RO - Well | RO - Nawasa | RO - Nawasa | Permeate #1 | Permeate #1 | Permeate #2 | Permeate #2 | Total Permeate | Brewhouse | Bottle Filler | Plant Cons
DATE | Supply (m3) | Consump. (m3) | Consump (m3) | Intake (m3) | Intake (m3) | Consump. (m3) | (m3) | Produced (m3) | (m3) | Produced (m3) | Produced (m3) | (m3) | (m3) | Tot.(Hl) | Comments | Total Prod. | Water
31 | [16 empty] | Hl/Hl
1 | 222322 | 183 | 183 | 56470 | 1336777 | 0 | 97122 | 0 | 1336777 | -1336777 | -1336777 | 0 | 0 | 366 |  |  | #DIV/0!
2 | 222505 | 285 | 147 | 0 | 1336777 | 138 | 97122 | 0 | 0 | 0 | 0 | 0 | 36 | 570 |  |  | #DIV/0!
3 | 222790 | 127 | -100 | 0 | 1336915 | 227 | 97122 | 0 | 0 | 0 | 0 | 0 | 29 | 254 |  |  | #DIV/0!
4 | 222917 | 347 | 173 | 0 | 1337142 | 174 | 97122 | 0 | 0 | 0 | 0 | 0 | 30 | 694 |  |  | #DIV/0!
5 | 223264 | 183 | -108 | 0 | 1337316 | 291 | 97122 | 0 | 0 | 0 | 0 | 0 | 24 | 366 |  |  | #DIV/0!
6 | 223447 | 89 | -167 | 0 | 1337607 | 256 | 97122 | 0 | 0 | 22492 | 22492 | 0 | 24 | 178 |  |  | #DIV/0!
7 | 223536 | 1 | -74 | 0 | 1337863 | 75 | 97122 | 0 | 22492 | -22492 | -22492 | 0 | 0 | 2 |  |  | #DIV/0!
8 | 223537 | 120 | -8 | 0 | 1337938 | 128 | 97122 | 0 | 0 | 0 | 0 | 0 | 17 | 240 |  |  | #DIV/0!
9 | 223657 | 206 | -15 | 0 | 1338066 | 221 | 97122 | 0 | 0 | 0 | 0 | 0 | 28 | 412 |  |  | #DIV/0!
10 | 223863 | 320 | 215 | 0 | 1338287 | 105 | 97122 | 0 | 0 | 0 | 0 | 0 | 25 | 640 |  |  | #DIV/0!
11 | 224183 | 402 | 231 | 0 | 1338392 | 171 | 97122 | 0 | 0 | 0 | 0 | 0 | 28 | 804 |  |  | #DIV/0!
12 | 224585 | 253 | 11 | 0 | 1338563 | 242 | 97122 | 0 | 0 | 0 | 0 | 0 | 30 | 506 |  |  | #DIV/0!
13 | 224838 | 176 | -48 | 0 | 1338805 | 224 | 97122 | 0 | 0 | 0 | 0 | 0 | 22 | 352 |  |  | #DIV/0!
14 | 225014 | 0 | -221 | 0 | 1339029 | 221 | 97122 | 0 | 0 | 0 | 0 | 0 | 3 | 0 |  |  | #DIV/0!
15 | 225014 | 47 | -4 | 0 | 1339250 | 51 | 97122 | 0 | 0 | 0 | 0 | 0 | 0 | 94 |  |  | #DIV/0!
16 | 225061 | 146 | 17 | 0 | 1339301 | 129 | 97122 | 0 | 0 | 0 | 0 | 0 | 8 | 292 |  |  | #DIV/0!
17 | 225207 | 8 | -32 | 0 | 1339430 | 40 | 97122 | 0 | 0 | 0 | 0 | 0 | 0 | 16 |  |  | #DIV/0!
18 | 225215 | 170 | 60 | 0 | 1339470 | 110 | 97122 | 0 | 0 | 0 | 0 | 0 | 27 | 340 |  |  | #DIV/0!
19 | 225385 | 363 | 193 | 0 | 1339580 | 170 | 97122 | 0 | 0 | 0 | 0 | 0 | 31 | 726 |  |  | #DIV/0!
20 | 225748 | 320 | 81 | 0 | 1339750 | 239 | 97122 | 0 | 0 | 0 | 0 | 0 | 29 | 640 |  |  | #DIV/0!
21 | 226068 | 146 | 25 | 0 | 1339989 | 121 | 97122 | 0 | 0 | 0 | 0 | 0 | 1 | 292 |  |  | #DIV/0!
22 | 226214 | 80 | -53 | 0 | 1340110 | 133 | 97122 | 0 | 0 | 0 | 0 | 0 | 0 | 160 |  |  | #DIV/0!
23 | 226294 | 85 | -166 | 0 | 1340243 | 251 | 97122 | 0 | 0 | 0 | 0 | 0 | 37 | 170 |  |  | #DIV/0!
24 | 226379 | 118 | -63 | 0 | 1340494 | 181 | 97122 | 0 | 0 | 0 | 0 | 0 | 28 | 236 |  |  | #DIV/0!
25 | 226497 | 219 | 3 | 0 | 1340675 | 216 | 97122 | 0 | 0 | 0 | 0 | 0 | 13 | 438 |  |  | #DIV/0!
26 | 226716 | 234 | 129 | 0 | 1340891 | 105 | 97122 | 0 | 0 | 0 | 0 | 0 | 5 | 468 |  |  | #DIV/0!
27 | 226950 | 140 | 67 | 0 | 1340996 | 73 | 97122 | 0 | 0 | 0 | 0 | 0 | 22 | 280 |  |  | #DIV/0!
28 | 227090 | 10 | -38 | 0 | 1341069 | 48 | 97122 | 0 | 0 | 0 | 0 | 0 | 0 | 20 |  |  | #DIV/0!
| 227100 |  | 0 |  | 1341117 |  | 97122
Total |  | 4778 | 438 |  |  | 4340 |  | 0 | 1359269 | -1336777 | -1336777 | 0 | 497 | 9556 | 0 | 0 | #DIV/0!